{"text_format":"3","workbook":"xlsb","n_sheets":23,"sheets":["Instrucciones","HE-4 SOLAR","Metasol","Perdidas","Datos CTE","Sombras","Tablas primario","Informe calculo","C. Primario","C. Secundario","Acumuladores","Captadores ANT","Disipadores","Fabricantes","Paneles","Compactos","Laboratorios","Localidad Usuario","Importacion","Posicion solar","Localidades","Datos SOLAR","Factor K"],"not_rendered":{"charts":14,"images":36,"macros":1,"external_links":1,"defined_names":233,"comments":5},"read":"bin_skipped_in_rows","date_system":"1900","formulas":"cached_only","passed_over":{"ids":[37,38,1024],"n":10779}}

{"sheet":"Instrucciones","index":0,"n_rows":142,"n_cols":10,"rows_kept":142,"merged":[[1,7,1,11],[3,9,3,11],[7,8,10,10]],"flags":["formulas_cached_only"]}
[]
[null,"1.- INTRODUCCIÓN DE DATOS",{"$nulls":5},"Autor: Oscar Redondo Rivera.       o.redondo.rivera@gmail.com"]
[]
[null,"Tan solo es necesario introducir datos en las casillas en color blanco.",{"$nulls":7},"Versión 5.7    Junio 2022"]
[null,"Las celdas en color azul con letra blanca señalan los datos que deben aportarse para el calculo"]
[null,"Las celdas en color azul claro con letra negra indican los datos que son calculados de forma automática"]
[]
[{"$nulls":8},"Nota: La presente aplicación se proporciona bajo una licencia Creative Commons \"tal cual\", sin garantías implícitas o explícitas. Bajo ninguna circunstancia el autor se responsabiliza de su uso.  "]
[]
[]
[]
[]
[]
[null,"2.- DATOS DE RADIACIÓN SOLAR"]
[]
[null,"Se ofrecen varias posibilidades:"]
[null,"a) Atlas de radiación solar 2012 de AEMET. Empleado por el CTE-HE4 para establecer las zonas de radiación solar (opción por defecto)"]
[null,"b) Datos de radición solar del Pliego de Instalaciones solares de baja temperatura del IDAE, más conservadoras que las anteriores"]
[null,"c) Cargas los datos de radiación desde los archivos generados por la plataforma PvGis"]
[null,"d) Definir por parte del usuario los datos de la localidad"]
[]
[null,"3.- ESTABLECER LA DEMANDA DE ACS SEGÚN CTE HE4 2013"]
[]
[null,"En primer lugar se establece como demnada principal la correspondiente a viviendas, "]
[null,"indicando el número de viviendas de que existen y su número de dormitorios"]
[null,"Se complementa la demanda con otros usos del edificio y se indica si el sistema de acumulación será centralizado o individual en cada vivienda"]
{"$rows_empty":15}
[null,"4.- AJUSTE DEL VOLUMEN EL NÚMERO DE PANELES SOLARES"]
[]
[null,"La selección del captador solar  desde el catalogos de la aplicación"]
[null,"El ajuste del nº de paneles se realiza desde el cursor         que actualiza de forma automatica el calculo y la gráfica de aporte solar"]
{"$rows_empty":14}
[null,"% Demanda neta: aporte solar contabilizando las perdidas de circuito y el sobrecalentamiento"]
[null,"% Demanda neta: aporte solar neto según método F-Chart"]
[]
[]
[null,"5.- AJUSTE DEL VOLUMEN DE ACUMULACIÓN"]
[]
[null,"Selección del volumen de acumulación, para lo que se aportarán datos del volumen óptimo, mínimo y máximo según el número de"]
[null,"paneles solares que se haya selccinado en el apartado anterior"]
[null,"En la parte inferior se selecciona el método de disipación, bien mediante aerotermo (dispador dinámico) o drain back"]
{"$rows_empty":15}
[null,"6.- SOMBRAS"]
[]
[null,"En la pestaña \"Sombras\" se dispone de las herramientas para establecer los perfiles de obstrucción solar sobre la carta solar cilíndrica"]
[null,"La herramienta cuenta con dos perfiles de posición relativa a los paneles (peto de cubierta y obstáculo superior) en los que se pedirán las "]
[null,"distancias relativas entre el obstáculo y los captadores. Adicionalmente se podrán incluir obstáculos genericos según su azimut (angulo respecto "]
[null,"al sur), distancia y altura de cada uno de sus vertices."]
[null,"El programa analizará la obstrucción solar y determinará de forma automática los factores de corrección"]
{"$rows_empty":20}
[null,"7.- CALCULO DEL CIRCUITO PRIMARIO"]
[]
[null,"Permite el calculo del circuito primario, incluido los datos de selección del equipo de bombeo y vaso de expansión si fuera necesario"]
[null,"El dimesionado se realiza en función del caudal de cada tramo que puede indicarse de forma directa (caudal adicional) o asociado a los "]
[null,"paneles solares (nº de captadores a los que da servicio el tramo)"]
{"$rows_empty":18}
[null,"INFORME DE SALIDA"]
[]
[null,"Informe de calculo editable que resume en una página las principales características del sitema calculado"]
[]
[]
[null,"IMPORTACIÓN DE DATOS DE LA PLATAFORMA PvGis"]
[]
[null,"Desde la pestaña \"Localidad de Usuario\" se ofrece enlace a la plataforma PvGis, donde obtener un archivo *.csv con datos de "]
[null,"Radiación Horizontal para cualquier localidad sobre 4 bases distintas de datos anuales"]

{"sheet":"HE-4 SOLAR","index":1,"n_rows":226,"n_cols":31,"rows_kept":226,"merged":[[1,1,1,8],[2,9,2,16],[3,9,3,16],[5,3,5,7],[8,9,8,16],[10,3,10,7],[10,9,10,16],[17,1,17,16],[17,18,17,25],[19,3,19,6],[20,3,20,6],[21,3,21,6],[26,3,26,5],[26,7,26,15],[27,7,27,8],[28,7,28,8],[29,7,29,8],[31,3,31,5],[31,7,31,10],[31,11,31,15],[32,7,32,10],[32,11,32,15],[34,3,34,5],[34,7,34,10],[34,11,34,15],[36,7,36,10],[36,11,36,15],[37,3,37,5],[37,7,37,8],[38,7,38,8],[45,18,58,18],[51,3,51,6],[52,3,52,6],[57,4,57,7],[58,5,58,7],[63,5,63,7],[78,3,78,6],[79,4,79,5],[80,3,80,6],[81,4,81,5],[83,8,83,16],[84,8,84,9],[86,3,86,6],[109,5,109,16],[112,3,112,7],[119,3,119,7],[184,3,184,5],[186,3,186,4],[190,4,190,5],[200,3,200,5],[202,3,202,4],[205,4,205,5],[208,4,208,5],[211,4,211,5],[213,3,213,5],[215,3,215,5],[217,3,217,5],[221,4,221,5],[222,4,222,5],[223,4,223,5],[224,4,224,5],[225,4,225,5]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":41}
[]
[null,"HE4 / 2019  CONTRIBUCION SOLAR MÍNIMA DE AGUA CALIENTE SANITARIA",{"$nulls":7},"Actualizaciones y otras herramientas en:"]
[{"$nulls":9},"Autor: Oscar Redondo Rivera.       o.redondo.rivera@gmail.com"]
[null,"DATOS GEOGRAFICOS Y CLIMATOLÓGICOS",{"$nulls":7},"Versión 5.7    Junio 2022"]
[]
[null,"Localidad",null,"Madrid",{"$nulls":5},"Latitud:",{"v":40.4,"d":"40.40º"}]
[null,"Zona climática s/ CTE-HE4",null,"IV"]
[null,"Zona Climática s/ CTE-HE1",null,"D3"]
[null,"Altura localidad (m)",null,655,null,"Altura capital: ",{"v":655,"d":"655 m"},null,null,""]
[]
[null,"Origen datos de radiación solar",null,"Atlas Radiacion solar 2012 AEMET",{"$nulls":4},0,""]
[]
[{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic.","Anual"]
[null,"Tª. media agua  red [ºC]:",null,{"v":8,"d":"8.00"},{"v":8,"d":"8.00"},{"v":10,"d":"10.00"},{"v":12,"d":"12.00"},{"v":14,"d":"14.00"},{"v":17,"d":"17.00"},{"v":20,"d":"20.00"},{"v":19,"d":"19.00"},{"v":17,"d":"17.00"},{"v":13,"d":"13.00"},{"v":10,"d":"10.00"},{"v":8,"d":"8.00"},{"v":13.03013698630137,"d":"13.03"},{"v":0,"d":"0.00"}]
[null,"Tª. media mensual en horas diurnas  [ºC]:",null,{"v":6.2,"d":"6.20"},{"v":7.4,"d":"7.40"},{"v":9.9,"d":"9.90"},{"v":12.2,"d":"12.20"},{"v":16,"d":"16.00"},{"v":20.7,"d":"20.70"},{"v":24.4,"d":"24.40"},{"v":23.9,"d":"23.90"},{"v":20.5,"d":"20.50"},{"v":14.7,"d":"14.70"},{"v":9.4,"d":"9.40"},{"v":6.4,"d":"6.40"},{"v":14.308333333333335,"d":"14.31"},{"v":0,"d":"0.00"}]
[null,"Rad. horiz. [MJ/m2 día]:",null,{"v":8.183804,"d":"8.18"},{"v":11.716899999999999,"d":"11.72"},{"v":16.76418,"d":"16.76"},{"v":20.7299,"d":"20.73"},{"v":23.79432,"d":"23.79"},{"v":27.904248,"d":"27.90"},{"v":28.985807999999995,"d":"28.99"},{"v":25.2364,"d":"25.24"},{"v":19.720444,"d":"19.72"},{"v":12.834512,"d":"12.83"},{"v":8.760636,"d":"8.76"},{"v":6.7417240000000005,"d":"6.74"},{"v":17.61440633333333,"d":"17.61"}]
[{"$nulls":3},248,224,310,360,434,510,620,589,510,403,300,248]
[null,"TIPO DE SISTEMA",{"$nulls":16},"COMPARATIVA BASES DE DATOS RADIACION HORIZONTAL MJ/m2 dia"]
[]
[null,"Tipo de sistema solar",null,"Colectivo Inter-acumulador central"]
[1,"Tipo de sistema de apoyo",null,"Combustion ",{"$nulls":3},"EP tot","EP nr","EP ren"]
[null,"Combustible sistema de apoyo",null,"Gas natural",{"$nulls":3},1.195,1.19,0.0050000000000001155]
[null,"Rendimiento sistema de apoyo",null,0.95,""]
[]
[null,"CALCULO DE NECESIDADES DE ACS"]
[]
[null,"Tipo de edificio",null,"Viviendas",{"$nulls":3},"Calculo del nº de ocupantes vivienda"]
[null,"Nº personas",null,64,{"$nulls":3},"Nº dormitorios",null,"1D","2D","3D","4D","5D","6D",">6D"]
[null,"Consumo por ocupante",null,{"v":28,"d":"28 l/d"},{"$nulls":3},"Nº pers (CTE)",null,1.5,3,4,5,6,6,7,"TOTAL"]
[null,"Factor de centralización",null,{"v":0.9,"d":"0.90"},{"$nulls":3},"Nº viviendas",null,0,0,16,0,0,0,0,16]
[{"$nulls":9},0,0,4,0,0,0,0]
[null,"Otros usos:",null,"Administrativos",{"$nulls":3},"Demanda de ACS viviendas",{"$nulls":3},{"v":1612.8,"d":"1,613 l/d"}]
[null,"Nº personas",null,0,2,null,null,"Demanda de ACS otros usos",{"$nulls":3},{"v":0,"d":"00 l/d"}]
[]
[null,"Otros usos:",null,"Restaurantes",{"$nulls":3},"Demanda TOTAL de ACS ",{"$nulls":3},{"v":1612.8,"d":"1,612.80 litros/dia de ACS a 60ºC"},{"$nulls":5},""]
[null,"Nº personas",null,0,8]
[{"$nulls":7},"Tipo de acumulación",{"$nulls":3},"Acumulación centralizada"]
[null,"Otros usos:",null,"Gimnasios",{"$nulls":3},"Nº dormitorios",null,"1D","2D","3D","4D","5D","6D",">6D"]
[null,"Nº personas",null,0,21,null,null,"Vol. Individual",null,"","",112,"","","",""]
[{"$nulls":9},0,0,1792,0,0,0,0,1792]
[{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic.","Anual"]
[null,"% Ocupación",null,{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"},{"v":1,"d":"100%"}]
[]
[null,"CAPTADORES. GEOMETRÍA Y CARACTERÍSTICAS",{"$nulls":18},{"v":0,"d":"0.00"},false,0]
[{"$nulls":20},{"v":0,"d":"0.00"}]
[null,"Ángulo de inclinación ( b )",null,{"v":40,"d":"40º"},"optimo",{"v":40.4,"d":"40º"},{"$nulls":14},{"v":0,"d":"0.00"}]
[null,"Azimut respecto a Sur ( a )",null,{"v":15,"d":"15º"},"optimo",{"v":0,"d":"0º"},{"$nulls":14},{"v":0,"d":"0.00"}]
[null,"Nº Captadores",null,14,{"$nulls":16},{"v":1,"d":"1.00"}]
[{"$nulls":20},{"v":1,"d":"1.00"},false,0]
[null,"Contribución anual del sistema",null,{"v":0.6219928289834757,"d":"62.20%"},"Min CTE",{"v":0.6,"d":"60%"},{"$nulls":14},{"v":1,"d":"1.00"}]
[{"$nulls":20},{"v":1,"d":"1.00"}]
[null,"Fabricante",null,"Saunier Duval",{"$nulls":16},{"v":0,"d":"0.00"}]
[null,"Modelo",null,"SRV 2.3"]
[]
[null,"Superficie de captación del panel (m²)",null,{"v":2.352,"d":"2.35"}]
[{"$nulls":20},{"v":0,"d":"0.00"}]
[null,"Número de grupos",null,2,{"$nulls":16},{"v":62.199282898347576,"d":"62.20"}]
[0,"Numero de paneles por grupo",null,{"v":7,"d":"7.00"},"",{"$nulls":15},{"v":37.800717101652424,"d":"37.80"}]
[null,"Numero de paneles en serie",null,0,null,"% Demanda Neta"]
[]
[null,"Fr(tα)'    Eficiencia óptica colector",null,{"v":0.79,"d":"0.790"},null,"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic.",null,"ANUAL",null,{"v":0,"d":"0.00"},false,0]
[null,"a1 Coeficiente lineal de perdidas (W/m²K)",null,{"v":2.4141,"d":"2.414"},null,{"v":0.30300361787342067,"d":"30.30%"},{"v":0.4640643912761879,"d":"46.41%"},{"v":0.6338774980388323,"d":"63.39%"},{"v":0.7153523066065581,"d":"71.54%"},{"v":0.7681160406471582,"d":"76.81%"},{"v":0.8777936280434953,"d":"87.78%"},{"v":0.9405594418575782,"d":"94.06%"},{"v":0.9151986134503998,"d":"91.52%"},{"v":0.8304987243104468,"d":"83.05%"},{"v":0.6051178385898652,"d":"60.51%"},{"v":0.39287638387983403,"d":"39.29%"},{"v":0.24019541573543163,"d":"24.02%"},0.94,{"v":0.6219928289834757,"d":"62.20%"},null,{"v":0,"d":"0.00"}]
[null,"a2 Coeficiente cuadr. de perdidas (W/m²K)",null,0.049]
[null,"FrUL  Coeficiente global de pérdida (W/m²K)",null,{"v":4.3741,"d":"4.374"},null,"% Demanda Bruta",null,null,"      no incluye perdidas termicas de circuito:",{"$nulls":4},{"v":0.09999999999999998,"d":"10.00%"}]
[]
[null,"Area total de captación proyectada",null,{"v":32.928,"d":"32.93m²"},null,{"v":0.4030036178734207,"d":"40.30%"},{"v":0.564064391276188,"d":"56.41%"},{"v":0.7338774980388323,"d":"73.39%"},{"v":0.8153523066065582,"d":"81.54%"},{"v":0.8681160406471582,"d":"86.81%"},{"v":0.9777936280434951,"d":"97.78%"},{"v":1.040559441857578,"d":"104.06%"},{"v":1.0151986134503999,"d":"101.52%"},{"v":0.9304987243104468,"d":"93.05%"},{"v":0.7051178385898653,"d":"70.51%"},{"v":0.49287638387983407,"d":"49.29%"},{"v":0.3401954157354316,"d":"34.02%"},null,{"v":0.7219928289834757,"d":"72.20%"}]
[]
[null,"VOLUMEN DE ACUMULACION"]
[]
[null,"Temperatura de acumulación ACS",null,{"v":60,"d":"60 ºC"}]
[null,"Demanda de ACS corregida s/ Tª",null,{"v":1612.8,"d":"1,613 l/d"}]
[]
[null,"Demanda de agua s/ ocupación",null,{"v":1612.8,"d":"1,613"},"V/A=",{"v":48.9795918367347,"d":"49"}]
[null,"Volumen de acumulación maximo",null,{"v":5927.039999999999,"d":"5,927"},"Valor en función del nº de paneles relación V/A=180",{"$nulls":7},""]
[null,"Volumen de acumulación mínimo",null,{"v":1646.3999999999999,"d":"1,646"},"Valor en función del nº de paneles relación V/A=50"]
[null,"Volumen de acumulación individual",null,"","",null,""]
[null,"Volumen de acumulación óptimo",null,{"v":2469.5999999999995,"d":"2470 l"},"Valor en función del nº de paneles relación V/A=75"]
[{"$nulls":20},"R mK/W","q W/m","q (W)","q total (W)","e(m):","λ :","A","clase","W(clase)",null,"W Epr"]
[null,"Acumulador 1",null,"SD Acumulador BDLE 2000",{"$nulls":3},"NO","",{"$nulls":3},1,"Altura",{"v":2,"d":"2.00"},"Radio",{"v":0.5641895835477563,"d":"0.56"},null,"Area(Uds)",{"v":9.089815403622064,"d":"9.09"},{"v":0.4013743199375991,"d":"0.40"},{"v":99.65759644567875,"d":"99.66"},{"v":255.54097072741536,"d":"255.54"},{"v":256,"d":"256.00"},"0,05","0,04",{"v":9.089815403622064,"d":"9.09"},"B",117,null,125]
[null,"nº acumuladores tipo 1",null,1,{"v":2000,"d":"2,000 litros"},{"$nulls":7},1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Acumulador 2",{"$nulls":5},"NO","",{"$nulls":3},1,"Altura",{"$error":"#DIV/0!"},"Radio",{"v":0,"d":"0.00"},null,"Area(Uds)",{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"v":0,"d":"0.00"},{"$error":"#DIV/0!"},{"v":0,"d":"0.00"},0,0,{"v":0,"d":"0.00"},null,0,null,0]
[null,"nº acumuladores tipo 2",null,null,{"v":0,"d":"00 litros"},null,null,"","","","","","",{"$nulls":10},{"v":256,"d":"256.00"},null,null,{"v":9.089815403622064,"d":"9.09"},null,{"v":117,"d":"117.00"},null,{"v":125,"d":"125.00"}]
[{"$nulls":7},"","","","","",""]
[null,"Volumen de acumulación proyectado",null,{"v":2000,"d":"2,000 l"},0,null,null,"",""]
[null,"Relación Volumen / Area de captación",null,{"v":60.738581146744416,"d":"60.74"},"Valor entre 50 y 180",{"$nulls":3},"CUMPLE"]
[]
[null,"Sistema de disipación de calor",null,"Sistema Drain-Back",{"$nulls":4},"Drain Back externo"]
[null,"Potencia mínima dispador",null,{"v":32,"d":"32 kW"},null,"PC (m.c.a):",0,null,"Caudal (l/h)",{"v":2400,"d":"2,400"}]
[]
[null,"FACTORES DE CORRECCIÓN DEL SISTEMA SOLAR"]
[]
[null,"Corecciones estándar IDAE - ASIT"]
[null,"MAI   Modificador del ángulo de incidencia",null,0.87,{"$nulls":3},"Densidad",1010,null,"Cp",3850,null,"Efectividad",0.7]
[null,"FIC   Corrección captador - intercambiador",null,"0,970",{"$nulls":3},"m",0.014027777777777778,null,"mCp",54.00694444444444,null,"FIC",0.9664537939113969]
[null,"CV            Correción volumen acumulación",null,{"v":1.0541420922471163,"d":"1.05"}]
[]
[null,"Correcciones adicionales",{"$nulls":3},"Activar"]
[null,"Factor corección por paneles en serie",null,{"v":1,"d":"1.00"},null,"SI"]
[]
[null,"Caudal de funcionamiento (l/h m2)",null,{"v":50,"d":"50.00"}]
[null,"Caudal de ensayo del panel (l/h m2)",null,48.97,null,"Activar"]
[null,"Factor corección por caudal",null,{"v":1.0012000697185506,"d":"1.00"},null,"SI"]
[]
[null,"Correccion TOTAL"]
[null,"Fr(tα)'    Eficiencia óptica corregida",null,{"v":0.667481063680033,"d":"0.667"},"factor:",{"v":0.8449127388354848,"d":"0.84"}]
[null,"Fr UL'    Coeficiente global corregido",null,{"v":4.477962664035537,"d":"4.478"},"factor:",{"v":1.0237449221635393,"d":"1.02"}]
[]
[null,"Perdida de radiación por sombras",{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic."]
[null,"% paneles afectados por sombras",null,{"v":1,"d":"100%"},"factor:",{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"}]
[{"$nulls":5},"Indica el porcentaje del total de paneles a los que afectan la obstruccion solar definida en la pestaña \"Sombras\""]
[null,"PERDIDAS TÉRMICAS POR ACUMULACIÓN"]
[]
[0,"Estimación valor UA deposito",null,"Sin pérdidas térmicas"]
[]
[0,"Perdida térmica estática",null,0,"W"]
[0,"Perdidas térmicas por acumulación",null,0,"Kwh/año",null,{"v":0,"d":"0.00%"},"% Demanda"]
[]
[null,"PERDIDAS TÉRMICAS DE CIRCUITO"]
[]
[1,"Estimación de perdidas térmicas",null,"Estimación SIMPLIFICADA"]
[]
[1,"Perdidas termicas primario",null,{"v":1135.4131611648,"d":"1,135"},"Kwh/año",null,{"v":0.0354,"d":"3.54%"},"SI",null,null,"Calculadas en C.Primario:",{"v":0.03536551266272243,"d":"3.54%"},{"v":1134.307020581792,"d":"1134"},"Kwh/año"]
[1,"Perdidas termicas secundario",null,{"v":70.5623998464,"d":"71"},"Kwh/año",null,{"v":0.0022,"d":"0.22%"},"SI",null,null,"Calculadas C. Secundario:",{"v":0.0025168454820914503,"d":"0.25%"},{"v":80.72484420861012,"d":"81"},"Kwh/año"]
[]
[1,"Perdidas termicas circuito consumo",null,{"v":481.10727167999994,"d":"481"},"Kwh/año",null,{"v":0.015,"d":"1.50%"},"SI"]
[]
[1,"Perdidas termicas distribución",null,{"v":160.36909056,"d":"160"},"Kwh/año",null,{"v":0.005,"d":"0.50%"},"SI"]
[1,"Perdidas termicas retorno",null,{"v":160.36909056,"d":"160"},"Kwh/año",null,{"v":0.005,"d":"0.50%"},"SI"]
[]
[null,"Perdidas termicas de circuito",null,{"v":3207.3818112,"d":"3,207"},"Kwh/año",null,{"v":0.1,"d":"10.00%"}]
[]
[null,"Perdidas termicas globales",null,{"v":3207.3818112,"d":"3,207"},"Kwh/año",null,{"v":0.1,"d":"10.00%"},"% Demanda"]
[]
[null,"CALCULO DE DEMANDA ENERGÉTICA"]
[]
[null,"Calculo de la Instalación por el método de curvas f (F-Chart). ",{"$nulls":10},"Yi relaciona las pérdidas del captador con la demanda de ACS"]
[null,"Ecuación de la fracción de carga calorífica mensual aportada:  f = 1,029Yi - 0,065Xi - 0,245Yi² + 0,0018Xi² + 0,215Yi³",{"$nulls":10},"Xi relaciona la energía absorbida con la demanda de ACS"]
[]
["1.-","DEMANDA NETA DE ACS"]
[{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic.","Anual"]
[null,"Días computables",null,31,28,31,30,31,30,31,31,30,31,30,31,365,"días/año"]
[null,"Consumo mensual de agua a 60º",null,{"v":49996.799999999996,"d":"49,997"},{"v":45158.4,"d":"45,158"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":588672,"d":"588,672"},"litros ACS/año"]
[null,"Consumo mensual corregido s/ Tª acumulación",null,{"v":49996.799999999996,"d":"49,997"},{"v":45158.4,"d":"45,158"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":588672,"d":"588,672"},"litros ACS/año"]
[null,"Incremento Ta. [ºC]:",null,{"v":52,"d":"52.00"},{"v":52,"d":"52.00"},{"v":50,"d":"50.00"},{"v":48,"d":"48.00"},{"v":46,"d":"46.00"},{"v":43,"d":"43.00"},{"v":40,"d":"40.00"},{"v":41,"d":"41.00"},{"v":43,"d":"43.00"},{"v":47,"d":"47.00"},{"v":50,"d":"50.00"},{"v":52,"d":"52.00"},{"v":46.96986301369863,"d":"46.97"},"ºC"]
[null,"(DEacs)  Demanda neta de ACS (kWh)",null,{"v":3015.8069759999994,"d":"3,016"},{"v":2723.9546880000003,"d":"2,724"},{"v":2899.8144,"d":"2,900"},{"v":2694.02112,"d":"2,694"},{"v":2667.829248,"d":"2,668"},{"v":2413.39392,"d":"2,413"},{"v":2319.8515199999997,"d":"2,320"},{"v":2377.847808,"d":"2,378"},{"v":2413.39392,"d":"2,413"},{"v":2725.8255359999994,"d":"2,726"},{"v":2806.272,"d":"2,806"},{"v":3015.8069759999994,"d":"3,016"},{"v":32073.818111999997,"d":"32,074"},"kWh/año"]
[{"$nulls":15},{"v":32073.818111999997,"d":"32,074"},"kWh/año"]
["2.-","ENERGIA ABSORBIDA POR CAPTADORES",null,1,2,3,4,5,6,7,8,9,10,11,12]
[{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic.","Anual",{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic."]
[null,"Días computables",null,31,28,31,30,31,30,31,31,30,31,30,31,365,"días",null,"kWh/mes sin perdidas",{"v":70.47164555555555,"d":"70.47"},{"v":91.13144444444444,"d":"91.13"},{"v":144.35821666666666,"d":"144.36"},{"v":172.74916666666667,"d":"172.75"},{"v":204.89553333333333,"d":"204.90"},{"v":232.53539999999998,"d":"232.54"},{"v":249.60001333333327,"d":"249.60"},{"v":217.31344444444443,"d":"217.31"},{"v":164.33703333333335,"d":"164.34"},{"v":110.51940888888888,"d":"110.52"},{"v":73.00529999999999,"d":"73.01"},{"v":58.053734444444444,"d":"58.05"}]
[null,"Rad. horiz. [kJ/m2/día]:",null,{"v":8.183804,"d":"8.18"},{"v":11.716899999999999,"d":"11.72"},{"v":16.76418,"d":"16.76"},{"v":20.7299,"d":"20.73"},{"v":23.79432,"d":"23.79"},{"v":27.904248,"d":"27.90"},{"v":28.985807999999995,"d":"28.99"},{"v":25.2364,"d":"25.24"},{"v":19.720444,"d":"19.72"},{"v":12.834512,"d":"12.83"},{"v":8.760636,"d":"8.76"},{"v":6.7417240000000005,"d":"6.74"},{"v":17.61440633333333,"d":"17.61"},"MJ/m² día",null,"kWh/mes sin sombras",{"v":97.18418707205971,"d":"97.18"},{"v":116.63378177208334,"d":"116.63"},{"v":166.13681902408334,"d":"166.14"},{"v":178.24431765833336,"d":"178.24"},{"v":193.11788195791664,"d":"193.12"},{"v":212.24784902700003,"d":"212.25"},{"v":235.25269256691658,"d":"235.25"},{"v":226.38220612291667,"d":"226.38"},{"v":197.28188382695836,"d":"197.28"},{"v":152.41220527600555,"d":"152.41"},{"v":108.64557489375,"d":"108.65"},{"v":85.24291070282779,"d":"85.24"}]
[null,"Factor de corrección por inclinación (k)",null,1.39,1.29,1.16,1.04,0.95,0.92,0.95,1.05,1.21,1.39,1.5,1.48,{"v":1.1941666666666668,"d":"1.19"},"factor",null,"Factor sombras 100%",{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"}]
[null,"Factor de corrección por orientación",null,{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.9921249999999998,"d":"0.99"},"factor",null,"kWh/mes con sombras 100%",{"v":97.18418707205971,"d":"97.18"},{"v":116.63378177208334,"d":"116.63"},{"v":166.13681902408334,"d":"166.14"},{"v":178.24431765833336,"d":"178.24"},{"v":193.11788195791664,"d":"193.12"},{"v":212.24784902700003,"d":"212.25"},{"v":235.25269256691658,"d":"235.25"},{"v":226.38220612291667,"d":"226.38"},{"v":197.28188382695836,"d":"197.28"},{"v":152.41220527600555,"d":"152.41"},{"v":108.64557489375,"d":"108.65"},{"v":85.24291070282779,"d":"85.24"}]
[null,"Factor de corrección por sombras ",null,{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},"factor",null,"kWh/mes con sombras según %",{"v":97.18418707205971,"d":"97.18"},{"v":116.63378177208334,"d":"116.63"},{"v":166.13681902408334,"d":"166.14"},{"v":178.24431765833336,"d":"178.24"},{"v":193.11788195791664,"d":"193.12"},{"v":212.24784902700003,"d":"212.25"},{"v":235.25269256691658,"d":"235.25"},{"v":226.38220612291667,"d":"226.38"},{"v":197.28188382695836,"d":"197.28"},{"v":152.41220527600555,"d":"152.41"},{"v":108.64557489375,"d":"108.65"},{"v":85.24291070282779,"d":"85.24"}]
[null,"Factor de corección total",null,{"v":1.37905375,"d":"1.38"},{"v":1.27984125,"d":"1.28"},{"v":1.150865,"d":"1.15"},{"v":1.0318100000000001,"d":"1.03"},{"v":0.94251875,"d":"0.94"},{"v":0.9127550000000001,"d":"0.91"},{"v":0.94251875,"d":"0.94"},{"v":1.04173125,"d":"1.04"},{"v":1.20047125,"d":"1.20"},{"v":1.37905375,"d":"1.38"},{"v":1.4881875,"d":"1.49"},{"v":1.468345,"d":"1.47"},{"v":1.1847626041666668,"d":"1.18"},"factor",null,"Factor sombra",{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"}]
[null,"Radiación solar incidente (KWh/m² mes)",null,{"v":97.18418707205971,"d":"97"},{"v":116.63378177208334,"d":"117"},{"v":166.13681902408334,"d":"166"},{"v":178.24431765833336,"d":"178"},{"v":193.11788195791664,"d":"193"},{"v":212.24784902700003,"d":"212"},{"v":235.25269256691658,"d":"235"},{"v":226.38220612291667,"d":"226"},{"v":197.28188382695836,"d":"197"},{"v":152.41220527600555,"d":"152"},{"v":108.64557489375,"d":"109"},{"v":85.24291070282779,"d":"85"},{"v":1968.7823099008515,"d":"1,969"},"KWh/m² año",null,"%paneles con sombra",{"v":1,"d":"100%"}]
[null,"Radiación solar incidente (KWh/mes)",null,{"v":3200.080911908782,"d":"3,200"},{"v":3840.51716619116,"d":"3,841"},{"v":5470.553176825016,"d":"5,471"},{"v":5869.2288918536005,"d":"5,869"},{"v":6358.985617110278,"d":"6,359"},{"v":6988.897172761056,"d":"6,989"},{"v":7746.400660843428,"d":"7,746"},{"v":7454.3132832154,"d":"7,454"},{"v":6496.0978706540845,"d":"6,496"},{"v":5018.6290953283105,"d":"5,019"},{"v":3577.4814901013997,"d":"3,577"},{"v":2806.878563622713,"d":"2,807"},{"v":64828.06390041522,"d":"64,828"},"KWh/año"]
[null,"Fr(tα)'    Eficiencia óptica corregida",null,{"v":0.6674810636800329,"d":"66.7%"},{"v":0.667481063680033,"d":"66.7%"},{"v":0.667481063680033,"d":"66.7%"},{"v":0.667481063680033,"d":"66.7%"},{"v":0.6674810636800329,"d":"66.7%"},{"v":0.667481063680033,"d":"66.7%"},{"v":0.667481063680033,"d":"66.7%"},{"v":0.667481063680033,"d":"66.7%"},{"v":0.6674810636800331,"d":"66.7%"},{"v":0.667481063680033,"d":"66.7%"},{"v":0.667481063680033,"d":"66.7%"},{"v":0.667481063680033,"d":"66.7%"},{"v":0.667481063680033,"d":"66.7%"},"%"]
[null,"Radiación solar absorvida (KWh/mes)",null,{"v":2135.9934109430437,"d":"2,136"},{"v":2563.4724831707017,"d":"2,563"},{"v":3651.490653385345,"d":"3,651"},{"v":3917.599143716023,"d":"3,918"},{"v":4244.502483634799,"d":"4,245"},{"v":4664.956518824925,"d":"4,665"},{"v":5170.575752791482,"d":"5,171"},{"v":4975.612959284814,"d":"4,976"},{"v":4336.022316473786,"d":"4,336"},{"v":3349.8398867653027,"d":"3,350"},{"v":2387.9011503085117,"d":"2,388"},{"v":1873.5382892675718,"d":"1,874"},{"v":43271.5050485663,"d":"43,272"},"KWh/año",null,"%perdida sombra",{"v":1,"d":"100%"}]
[{"$nulls":3},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},null,{"v":1,"d":"1.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":43271.5050485663,"d":"43,272"},"kWh/año"]
["3.-","CALCULO APORTE SOLAR NETO",null,0,0,0,0,0,0,0,0,0,0,0,0,0]
[{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic.","Anual"]
[null,"Relación  radiación absorvida y ener. demandada",null,{"v":0.7082659559916888,"d":"0.71"},{"v":0.9410848478734686,"d":"0.94"},{"v":1.259215297842974,"d":"1.26"},{"v":1.4541827881869103,"d":"1.45"},{"v":1.590994808538361,"d":"1.59"},{"v":1.9329445061438313,"d":"1.93"},{"v":2.2288390908705584,"d":"2.23"},{"v":2.0924858784254092,"d":"2.09"},{"v":1.796649225201407,"d":"1.80"},{"v":1.228926738899442,"d":"1.23"},{"v":0.8509157880307082,"d":"0.85"},{"v":0.6212394573582856,"d":"0.62"},{"v":1.349122355731538,"d":"1.35"},"valor Yi"]
[null,"Factor de corrección por consumo Tª ACS",null,{"v":1.054328358208955,"d":"1.05"},{"v":1.03792656587473,"d":"1.04"},{"v":1.0880355160932298,"d":"1.09"},{"v":1.1436902050113895,"d":"1.14"},{"v":1.1823809523809523,"d":"1.18"},{"v":1.260983606557377,"d":"1.26"},{"v":1.3623280423280424,"d":"1.36"},{"v":1.3178975032851514,"d":"1.32"},{"v":1.2636477987421382,"d":"1.26"},{"v":1.154466588511137,"d":"1.15"},{"v":1.094834437086093,"d":"1.09"},{"v":1.0516239316239315,"d":"1.05"},{"v":1.1611513616702123,"d":"1.16"},"valor Cti"]
[null,"Energia mensual perdida por el campo captador",null,{"v":10849.194199880296,"d":"10,849"},{"v":9523.414979531794,"d":"9,523"},{"v":10754.410752736869,"d":"10,754"},{"v":10660.589861508277,"d":"10,661"},{"v":10895.708298941425,"d":"10,896"},{"v":10616.000874276824,"d":"10,616"},{"v":11298.537949301,"d":"11,299"},{"v":11002.339676977785,"d":"11,002"},{"v":10665.261088742047,"d":"10,665"},{"v":10803.118913074462,"d":"10,803"},{"v":10530.64481300519,"d":"10,531"},{"v":10798.291978266232,"d":"10,798"},{"v":128397.51338624221,"d":"128,398"},"KWh/año"]
[null,"Relación entre energía perdida y demanda mensual",null,{"v":3.5974431673575045,"d":"3.60"},{"v":3.496172319417008,"d":"3.50"},{"v":3.7086548548544584,"d":"3.71"},{"v":3.9571292824565076,"d":"3.96"},{"v":4.084110070803686,"d":"4.08"},{"v":4.398784958518841,"d":"4.40"},{"v":4.870371164660143,"d":"4.87"},{"v":4.627015925898057,"d":"4.63"},{"v":4.419196137173515,"d":"4.42"},{"v":3.9632466459784697,"d":"3.96"},{"v":3.7525388889620075,"d":"3.75"},{"v":3.5805646927007553,"d":"3.58"},{"v":4.003187675938213,"d":"4.00"},"valor Xi"]
[null,"Porcentaje demanda aportado por sistema solar",null,{"v":0.4030036178734207,"d":"40.3%"},{"v":0.564064391276188,"d":"56.4%"},{"v":0.7338774980388323,"d":"73.4%"},{"v":0.8153523066065582,"d":"81.5%"},{"v":0.8681160406471582,"d":"86.8%"},{"v":0.9777936280434951,"d":"97.8%"},{"v":1.040559441857578,"d":"104.1%"},{"v":1.0151986134503999,"d":"101.5%"},{"v":0.9304987243104468,"d":"93.0%"},{"v":0.7051178385898653,"d":"70.5%"},{"v":0.49287638387983407,"d":"49.3%"},{"v":0.3401954157354316,"d":"34.0%"},{"v":0.7219928289834757,"d":"72.20%"},"Fracción F-chart"]
[{"$nulls":3},{"v":1215.3811221359001,"d":"1,215"},{"v":1536.4858429506387,"d":"1,536"},{"v":2128.108536648978,"d":"2,128"},{"v":2196.576334238783,"d":"2,197"},{"v":2315.9853638964455,"d":"2,316"},{"v":2359.8011969349127,"d":"2,360"},{"v":2413.943402843654,"d":"2,414"},{"v":2413.9877976776725,"d":"2,414"},{"v":2245.6599638185885,"d":"2,246"},{"v":1922.0282103173806,"d":"1,922"},{"v":1383.1451955432296,"d":"1,383"},{"v":1025.9637079781346,"d":"1,026"}]
[null,"Balance térmico:   DEacs = ESnet + EAnet;   ESnet = ESpro - PTdem;   Fraccion(%) = ESnet / DEacs"]
[null,"(DEacs)  Demanda neta de ACS (kWh)",null,{"v":3015.8069759999994,"d":"3,016"},{"v":2723.9546880000003,"d":"2,724"},{"v":2899.8144,"d":"2,900"},{"v":2694.02112,"d":"2,694"},{"v":2667.829248,"d":"2,668"},{"v":2413.39392,"d":"2,413"},{"v":2319.8515199999997,"d":"2,320"},{"v":2377.847808,"d":"2,378"},{"v":2413.39392,"d":"2,413"},{"v":2725.8255359999994,"d":"2,726"},{"v":2806.272,"d":"2,806"},{"v":3015.8069759999994,"d":"3,016"},{"v":32073.818111999997,"d":"32,074"},"kWh/año"]
[null,"(ESpro) Energía Solar Térmica Producida (kWh)",null,{"v":1215.3811221359001,"d":"1,215"},{"v":1536.4858429506387,"d":"1,536"},{"v":2128.108536648978,"d":"2,128"},{"v":2196.576334238783,"d":"2,197"},{"v":2315.9853638964455,"d":"2,316"},{"v":2359.8011969349127,"d":"2,360"},{"v":2413.943402843654,"d":"2,414"},{"v":2413.9877976776725,"d":"2,414"},{"v":2245.6599638185885,"d":"2,246"},{"v":1922.0282103173806,"d":"1,922"},{"v":1383.1451955432296,"d":"1,383"},{"v":1025.9637079781346,"d":"1,026"},{"v":23157.06667498432,"d":"23,157"},"kWh/año"]
[null,"(PTdem) Perdidas Térmicas asociadas (kWh)",null,{"v":301.58069759999995,"d":"302"},{"v":272.39546880000006,"d":"272"},{"v":289.98144,"d":"290"},{"v":269.402112,"d":"269"},{"v":266.7829248,"d":"267"},{"v":241.339392,"d":"241"},{"v":231.98515199999997,"d":"232"},{"v":237.78478080000002,"d":"238"},{"v":241.339392,"d":"241"},{"v":272.5825535999999,"d":"273"},{"v":280.6272,"d":"281"},{"v":301.58069759999995,"d":"302"},{"v":3207.3818111999994,"d":"3,207"},"kWh/año"]
[null,"(ESnet) Aporte Solar Neto (kWh) ",null,{"v":913.8004245359002,"d":"914"},{"v":1264.0903741506386,"d":"1,264"},{"v":1838.1270966489778,"d":"1,838"},{"v":1927.1742222387832,"d":"1,927"},{"v":2049.2024390964457,"d":"2,049"},{"v":2118.461804934913,"d":"2,118"},{"v":2181.9582508436542,"d":"2,182"},{"v":2176.2030168776723,"d":"2,176"},{"v":2004.3205718185884,"d":"2,004"},{"v":1649.4456567173806,"d":"1,649"},{"v":1102.5179955432295,"d":"1,103"},{"v":724.3830103781347,"d":"724"},{"v":19949.68486378432,"d":"19,950"},"kWh/año"]
[null,"Fracción de DEMANDA ANUAL ACS",null,{"v":0.30300361787342067,"d":"30.3%"},{"v":0.4640643912761879,"d":"46.4%"},{"v":0.6338774980388323,"d":"63.4%"},{"v":0.7153523066065581,"d":"71.5%"},{"v":0.7681160406471582,"d":"76.8%"},{"v":0.8777936280434953,"d":"87.8%"},{"v":0.9405594418575782,"d":"94.1%"},{"v":0.9151986134503998,"d":"91.5%"},{"v":0.8304987243104468,"d":"83.0%"},{"v":0.6051178385898652,"d":"60.5%"},{"v":0.39287638387983403,"d":"39.3%"},{"v":0.24019541573543163,"d":"24.0%"},{"v":0.6219928289834757,"d":"62.20%"},"kWh/año",null,null,0]
[null,"(EAnet) Aporte neto sistema apoyo (kWh) ",null,{"v":2102.006551464099,"d":"2,102"},{"v":1459.8643138493617,"d":"1,460"},{"v":1061.6873033510224,"d":"1,062"},{"v":766.8468977612167,"d":"767"},{"v":618.6268089035543,"d":"619"},{"v":294.93211506508715,"d":"295"},{"v":137.89326915634547,"d":"138"},{"v":201.64479112232766,"d":"202"},{"v":409.0733481814116,"d":"409"},{"v":1076.3798792826187,"d":"1,076"},{"v":1703.7540044567704,"d":"1,704"},{"v":2291.4239656218647,"d":"2,291"},{"v":12124.133248215676,"d":"12,124"},"kWh/año"]
[]
[null,"EP renovable sistema solar",null,{"v":913.8004245359002,"d":"914"},{"v":1264.0903741506386,"d":"1,264"},{"v":1838.1270966489778,"d":"1,838"},{"v":1927.1742222387832,"d":"1,927"},{"v":2049.2024390964457,"d":"2,049"},{"v":2118.461804934913,"d":"2,118"},{"v":2181.9582508436542,"d":"2,182"},{"v":2176.2030168776723,"d":"2,176"},{"v":2004.3205718185884,"d":"2,004"},{"v":1649.4456567173804,"d":"1,649"},{"v":1102.5179955432295,"d":"1,103"},{"v":724.3830103781347,"d":"724"},{"v":19949.68486378432,"d":"19,950"},"kWh/año"]
[null,"EP renovable sistema apoyo",null,{"v":10.510032757320738,"d":"10.51"},{"v":7.299321569246977,"d":"7.30"},{"v":5.3084365167552345,"d":"5.31"},{"v":3.8342344888061723,"d":"3.83"},{"v":3.0931340445178432,"d":"3.09"},{"v":1.4746605753254698,"d":"1.47"},{"v":0.6894663457817433,"d":"0.69"},{"v":1.0082239556116617,"d":"1.01"},{"v":2.045366740907105,"d":"2.05"},{"v":5.381899396413218,"d":"5.38"},{"v":8.518770022284048,"d":"8.52"},{"v":11.457119828109589,"d":"11.46"},{"v":60.620666241079796,"d":"61"},"kWh/año"]
[null,"EP renovable total",null,{"v":924.3104572932209,"d":"924"},{"v":1271.3896957198856,"d":"1,271"},{"v":1843.435533165733,"d":"1,843"},{"v":1931.0084567275894,"d":"1,931"},{"v":2052.2955731409634,"d":"2,052"},{"v":2119.936465510238,"d":"2,120"},{"v":2182.647717189436,"d":"2,183"},{"v":2177.211240833284,"d":"2,177"},{"v":2006.3659385594956,"d":"2,006"},{"v":1654.8275561137937,"d":"1,655"},{"v":1111.0367655655136,"d":"1,111"},{"v":735.8401302062443,"d":"736"},{"v":20010.305530025402,"d":"20,010"}]
[null,"EP NO renovable sistema apoyo",null,{"v":2501.387796242278,"d":"2,501"},{"v":1737.2385334807402,"d":"1,737"},{"v":1263.4078909877167,"d":"1,263"},{"v":912.5478083358479,"d":"913"},{"v":736.1659025952296,"d":"736"},{"v":350.9692169274537,"d":"351"},{"v":164.0929902960511,"d":"164"},{"v":239.95730143556992,"d":"240"},{"v":486.79728433587974,"d":"487"},{"v":1280.8920563463162,"d":"1,281"},{"v":2027.4672653035568,"d":"2,027"},{"v":2726.7945190900186,"d":"2,727"},{"v":14427.71856537666,"d":"14,428"},"kWh/año"]
[null,"ENERGÍA PRIMARIA total",null,{"v":3425.698253535499,"d":"3,426"},{"v":3008.628229200626,"d":"3,009"},{"v":3106.8434241534496,"d":"3,107"},{"v":2843.5562650634374,"d":"2,844"},{"v":2788.461475736193,"d":"2,788"},{"v":2470.9056824376917,"d":"2,471"},{"v":2346.7407074854873,"d":"2,347"},{"v":2417.1685422688543,"d":"2,417"},{"v":2493.1632228953754,"d":"2,493"},{"v":2935.7196124601096,"d":"2,936"},{"v":3138.5040308690704,"d":"3,139"},{"v":3462.634649296263,"d":"3,463"},{"v":34438.02409540206,"d":"34,438"},"kWh/año"]
[null,"Fracción de ENERGÍA PRIMARIA cubierta",null,{"v":0.2698166589364035,"d":"26.98%"},{"v":0.4225811894538017,"d":"42.26%"},{"v":0.593346777257702,"d":"59.33%"},{"v":0.6790822043693622,"d":"67.91%"},{"v":0.7359956703720028,"d":"73.60%"},{"v":0.8579592821280001,"d":"85.80%"},{"v":0.9300762160162657,"d":"93.01%"},{"v":0.9007279396370366,"d":"90.07%"},{"v":0.8047471261145311,"d":"80.47%"},{"v":0.5636871958378414,"d":"56.37%"},{"v":0.35400201963668054,"d":"35.40%"},{"v":0.21250874109857204,"d":"21.25%"},{"v":0.5810526607041036,"d":"58.11%"},"valor f en %"]
[]
[null,"CUMPLIMIENTO CTE DB-HE4 / 2013"]
[]
["1.-","CONTRIBUCIÓN SOLAR MÍNIMA",null,"CTE-HE4 Tabla 2.1"]
[]
[null,"Capital de Provincia",null,"Madrid"]
[null,"Zona climática",null,"IV"]
[1,"Demanda total de agua caliente sanitaria",null,{"v":1612.8,"d":"1613 l/d"}]
[null,"Contribución solar anual mínima (%)",null,{"v":0.6,"d":"60.00%"}]
[null,"Contribución Demanda total solar anual (%)",null,{"v":0.6219928289834757,"d":"62.20%"},"CUMPLE",null,""]
[]
[null,"DESGLOSE DE PERDIDAS CONSIDERADAS"]
[]
[null,"Perdidas por acumulación",null,{"v":0,"d":"0.00%"}]
[null,"Perdidas en circuitos (distribución y retorno)",null,{"v":0.1,"d":"10.00%"}]
[null,"Perdidas GLOBALES",null,{"v":0.1,"d":"10.00%"}]
[]
[null,"COMPROBACIONES DE DISEÑO DEL SISTEMA SOLAR"]
[]
["1.-","PERDIDAS LÍMITE",null,"Opcional"]
[]
[2,"Disposición de los paneles",null,"Superposición"]
[]
[null,"Perdida límite por orientación e inclinación",null,{"v":0.2,"d":"20.00%"}]
[null,"Perdida calculada por orientación e inclinación",null,{"v":0.0078942,"d":"0.79%"},"CUMPLE"]
[]
[null,"Perdida límite por sombras",null,{"v":0.15,"d":"15.00%"}]
[null,"Perdida calculada por sombras",null,{"v":0,"d":"0.00%"},"CUMPLE"]
[]
[null,"Perdida límite TOTAL",null,{"v":0.3,"d":"30.00%"}]
[null,"Perdida calculada TOTAL",null,{"v":0.0078942,"d":"0.79%"},"CUMPLE"]
[]
["2.-","EXCESO DE CONTRIBUCIÓN SOLAR",null,"Opcional"]
[]
[null,"Ningún mes supera una contribucion del 110%",null,"CUMPLE",null,null,0]
[null,"No se supera el 100% de contribución "]
[null,"en más de 3 meses seguidos",null,"CUMPLE",null,null,0]
[]
["3.-","RANGO ACEPTACIÓN METODO F-CHART",null,"Datos infomativos sobre el rango de aplicación del método F-CHart"]
[]
[null,"Eficiencia óptica corregida",null,{"v":0.667481063680033,"d":"0.67"},"CUMPLE",null,"Rango 0,6 a 0,9"]
[null,"FR * Área de captación",null,{"v":61.07880974332553,"d":"61.08"},"CUMPLE",null,"Rango 5 a 120 m2"]
[null,"Coeficiente perdidas térmicas",null,{"v":2.4141,"d":"2.41"},"CUMPLE",null,"Rango 2,1 a 8,3"]
[null,"Inclinación captadores",null,{"v":40,"d":"40.00"},"CUMPLE",null,"Rango 30 a 90 grados"]
[null,"Razón de acumulación  V/A",null,{"v":60.738581146744416,"d":"60.74"},"CUMPLE",null,"Rango 37,5 a 300"]

{"sheet":"Metasol","index":2,"n_rows":85,"n_cols":27,"rows_kept":85,"hidden":true,"merged":[[26,0,28,0],[30,0,39,0],[41,0,56,0]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":21}
[{"$nulls":9},"SCH104","SCH102","SCH202","SCH203","SCH204","SCH207"]
[null,"metodos","esquemas","tipo","inter. Ext",null,null,"Metasol",1,-0.1735283869,{"v":-0.52849918841,"d":"-0.5284991884"},"‐0,871382",{"v":-1.909441585452,"d":"-1.9094415855"},"‐0,7355038529 ",{"v":0.137245791209,"d":"0.1372457912"},1,null,"Acumulación centralizada"]
[null,"F-Chart","Individual con Inter-acumulador",1,0,"Acumulación individual",null,"SCH102","Ln F1",1.1269537804,{"v":1.06087912985,"d":"1.0608791299"},0.7765256126,{"v":0.889813075151,"d":"0.8898130752"},0.8994982207,{"v":0.956114873607,"d":"0.9561148736"},2,null,"Acumulación individual"]
[null,"Metasol","Individual con Intercambiador",2,1,"Acumulación individual",null,"SCH104","Ln A3",-0.0912676768,-0.0200822197,0.3755628305,{"v":0.272078600786,"d":"0.2720786008"},0.2268873494,{"v":-0.018375323935,"d":"-0.0183753239"},3]
[]
[null,null,"Individual compacto Termosifón",1,0,"Acumulación individual",null,"SCH102"]
[null,null,"Individual compacto Drain Back",1,1,"Acumulación individual",null,"SCH102"]
[]
[null,null,"Colectivo Inter-acumulador central",3,0,"Acumulación centralizada",null,"SCH204","A2/A3",{"v":-22.9836361,"d":"-22.98363610"},{"v":-23.32442494564,"d":"-23.32442495"},"‐12,1873338774 ",{"v":-24.212694470047,"d":"-24.2126944700"},"‐27,7105927846",{"v":-26.258300208451,"d":"-26.2583002085"},4]
[null,null,"Colectivo Intercambiador central",3,1,"Acumulación centralizada"]
[null,null,"Colectivo ACS Centralizada",4,1,"Acumulación centralizada",null,"SCH207","A1",-0.0459984729,{"v":-0.07211289118,"d":"-0.0721128912"},"‐0,0326128867 ",{"v":-0.035478513849,"d":"-0.0354785138"},"‐0,0371476456 ",{"v":-0.05729495211,"d":"-0.0572949521"},5]
[null,null,"Colectivo Acumulacion distribuida",5,0,"Acumulación individual",null,"SCH202","A5",-1.4155198442,{"v":-3.063406565,"d":"-3.0634065650"},"‐0,7190799715 ",{"v":-0.681774411617,"d":"-0.6817744116"},"‐0,8663818373",{"v":-1.727465587297,"d":"-1.7274655873"},6]
[null,null,"Colectivo Intercambio distribuido",6,1,"Acumulación centralizada",null,"SCH203","A4",0.8250408319,{"v":2.06557416941,"d":"2.0655741694"},"‐0,0608396520 ",{"v":0.015113328142,"d":"0.0151133281"},1.1404850555,{"v":0.796922801242,"d":"0.7969228012"},7]
[{"$nulls":8},"X2",-0.0659330606,{"v":-0.06270279009,"d":"-0.0627027901"},0.0271102764,{"v":-0.045338520315,"d":"-0.0453385203"},"‐0,0917823944",{"v":-0.053032742772,"d":"-0.0530327428"},8]
[null,"Selección","Colectivo Inter-acumulador central",3,0,"Acumulación centralizada",null,"SCH204","X3",{"v":-0.058197127,"d":"-0.0581971270"},{"v":-0.03782807509,"d":"-0.0378280751"},"‐0,0412086010 ",{"v":-0.026270206406,"d":"-0.0262702064"},"‐0,0091913509 ",{"v":-0.035093339147,"d":"-0.0350933391"},9]
[{"$nulls":8},"X4",{"v":-0.014030316,"d":"-0.0140303160"},{"v":-0.01152248139,"d":"-0.0115224814"},"‐0,0213528197 ",{"v":0.054914615086,"d":"0.0549146151"},0.0546786339,{"v":0.062140921982,"d":"0.0621409220"},10]
[{"$nulls":3},"inter. Ext",{"$nulls":4},"Ln A6",null,null,"‐0,0438146316",{"v":-0.163478373,"d":"-0.1634783730"},"‐0,1494371856",{"v":0.052318897,"d":"0.0523188970"},11]
[null,null,"Individual con Inter-acumulador",0,{"$nulls":4},"LnA7",{"$nulls":3},{"v":0.09388373,"d":"0.0938837300"},null,null,12]
[null,null,"Individual con Intercambiador",1,{"$nulls":4},"Ln A8",null,null,"‐0,0919794803",{"$nulls":3},13]
[null,null,"Colectivo Inter-acumulador central",{"$nulls":5},"Ln F3",{"$nulls":3},{"v":0.086174831,"d":"0.0861748310"},0.0643562705,{"v":0.031928505,"d":"0.0319285050"},14]
[null,null,"Colectivo ACS Centralizada",{"$nulls":5},"Ln A9",{"$nulls":5},{"v":-0.290530107,"d":"-0.2905301070"},15]
[null,null,"Colectivo Acumulacion distribuida",{"$nulls":5},"F1 x F2",{"$nulls":3},{"v":9.757870000000001e-07,"d":"0.0000009758"},{"v":8.87e-07,"d":"0.0000008870"},{"v":8.43014e-07,"d":"0.0000008430"},16]
[null,null,"Colectivo Intercambio distribuido",{"$nulls":10}," "]
[]
[]
[{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic.","Anual",null,null,"Calculo A0 y A1"]
["Var. Ext.","F1","Rad. incidente kWh/mes",{"v":2135.9934109430437,"d":"2,136"},{"v":2563.4724831707017,"d":"2,563"},{"v":3651.490653385345,"d":"3,651"},{"v":3917.599143716023,"d":"3,918"},{"v":4244.502483634799,"d":"4,245"},{"v":4664.956518824925,"d":"4,665"},{"v":5170.575752791482,"d":"5,171"},{"v":4975.612959284814,"d":"4,976"},{"v":4336.022316473786,"d":"4,336"},{"v":3349.8398867653027,"d":"3,350"},{"v":2387.9011503085117,"d":"2,388"},{"v":1873.5382892675718,"d":"1,874"},{"v":43271.5050485663,"d":"43,272"},"kWh/año",null,"Captador","Saunier Duval"]
[null,"F2","Temp. Ambiente",{"v":6.2,"d":"6.20"},{"v":7.4,"d":"7.40"},{"v":9.9,"d":"9.90"},{"v":12.2,"d":"12.20"},{"v":16,"d":"16.00"},{"v":20.7,"d":"20.70"},{"v":24.4,"d":"24.40"},{"v":23.9,"d":"23.90"},{"v":20.5,"d":"20.50"},{"v":14.7,"d":"14.70"},{"v":9.4,"d":"9.40"},{"v":6.4,"d":"6.40"},{"v":14.308333333333335,"d":"14.31"},"ºC media",null,"a0 Rendimiento óptico",0.79,"adimensional"]
[null,"F3","Temp. Agua red",{"v":8,"d":"8.00"},{"v":8,"d":"8.00"},{"v":10,"d":"10.00"},{"v":12,"d":"12.00"},{"v":14,"d":"14.00"},{"v":17,"d":"17.00"},{"v":20,"d":"20.00"},{"v":19,"d":"19.00"},{"v":17,"d":"17.00"},{"v":13,"d":"13.00"},{"v":10,"d":"10.00"},{"v":8,"d":"8.00"},{"v":17.61440633333333,"d":"17.61"},"ºC media",null,"a1 lineal orden 1",2.4141,"W/m2K"]
[{"$nulls":18},"Caudal test ensayo",48.97,"Kg/h","den",{"v":1057.66,"d":"1,057.66"}," Kg/m³"]
["Variables   sistema","A0","rend. óptico captador",{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.7756542743812971,"d":"0.78"},null,null,"Cp fluido ensayo",{"v":3.5,"d":"3.50"},"KJ/KgK","Ce",{"v":3.8,"d":"3.800"},"KJ/kgK."]
[null,"A1","coef. Lineal campo",{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},{"v":2.2991320224689242,"d":"2.30"},null,null,"Sup absorvedor",2.352,"m2","Cp",{"v":4.019108,"d":"4.019"},"KJ/Kgm3"]
[null,"A2","Área absorvedor (m2)",{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},{"v":32.928,"d":"32.93"},null,null,"Sup apertura",2.352,"m2"]
[null,"A3","Demanda ACS (kWh)",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"}]
[null,"A4","VOL/A2  (m3/m2)",{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},{"v":60.738581146744416,"d":"60.74"},null,null,"Factores de arrastre"]
[null,"A5","Coeficiente orden 2",{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},null,null,"FR alfa",{"v":0.777127680585588,"d":"0.78"}]
[null,"A6","pérdidas circuito distrib.",{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},null,null,"FR UL",{"v":2.3747644730400856,"d":"2.37"}]
[null,"A7","potencia interc. Individual",{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},{"v":10,"d":"10.00"},"kW",">>>","farrastre",{"v":0.9837059247918836,"d":"0.98"},"Corrige la diferencia entre ensayo y proyecto"]
[null,"A8","pérdidas acm. individuales ",{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"},{"v":5,"d":"5.00"}]
[null,"A9","temperatura de distribución",{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"},{"v":60,"d":"60.00"}]
[{"$nulls":18},"Corrección fluido primario empleado"]
["Factores","1",null,"‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ","‐0,7355038529 ",null,null,"Caudal primario",{"v":52.88300000000001,"d":"52.88"},"Kg/h","den",{"v":1057.66,"d":"1,057.66"}," Kg/m³"]
[null,"Ln F1",null,0.8994982207,0.8994982207,0.8994982207,0.8994982207,0.8994982207,0.8994982207,0.8994982207,0.8994982207,0.8994982207,0.8994982207,0.8994982207,0.8994982207,0.8994982207,null,null,"Cp fluido primario",{"v":3.5,"d":"3.50"},"KJ/KgK","Ce",{"v":3.8,"d":"3.800"},"KJ/kgK."]
[null,"Ln A3",null,0.2268873494,0.2268873494,0.2268873494,0.2268873494,0.2268873494,0.2268873494,0.2268873494,0.2268873494,0.2268873494,0.2268873494,0.2268873494,0.2268873494,0.2268873494,null,null,"r sistema",{"v":0.9850622164382551,"d":"0.99"},null,"Cp",{"v":4.019108,"d":"4.019"},"KJ/Kgm3"]
[null,"A2/A3",null,0,0,0,0,0,0,0,0,0,0,0,0,0,null,null,"r ensayo",{"v":0.9838814900553972,"d":"0.98"}]
[null,"A1",null,0,0,0,0,0,0,0,0,0,0,0,0,0,null,">>>","r",{"v":1.0012000697185506,"d":"1.00"},"Corrige la relación entre caudal de ensayo y proyecto"]
[null,"A5",null,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"A4",null,0,0,0,0,0,0,0,0,0,0,0,0,0,null,null,"Corrección num captadores en serie"]
[null,"X2",null,"‐27,7105927846","‐27,7105927846","‐27,7105927846","‐27,7105927846","‐27,7105927846","‐27,7105927846","‐27,7105927846","‐27,7105927846","‐27,7105927846","‐27,7105927846","‐27,7105927846","‐27,7105927846","‐27,7105927846",null,null,"num captadores serie",0]
[null,"X3",null,0,0,0,0,0,0,0,0,0,0,0,0,0,null,null,"K",{"v":0.012830288280814442,"d":"0.0128"}]
[null,"X4",null,"‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ","‐0,0371476456 ",null,">>>","fserie",{"v":1,"d":"1.00"},"Corrige la presencia de enlaces en serie"]
[null,"Ln A6",null,"‐0,8663818373","‐0,8663818373","‐0,8663818373","‐0,8663818373","‐0,8663818373","‐0,8663818373","‐0,8663818373","‐0,8663818373","‐0,8663818373","‐0,8663818373","‐0,8663818373","‐0,8663818373","‐0,8663818373"]
[null,"LnA7",null,1.1404850555,1.1404850555,1.1404850555,1.1404850555,1.1404850555,1.1404850555,1.1404850555,1.1404850555,1.1404850555,1.1404850555,1.1404850555,1.1404850555,1.1404850555]
[null,"Ln A8",null,"‐0,0917823944","‐0,0917823944","‐0,0917823944","‐0,0917823944","‐0,0917823944","‐0,0917823944","‐0,0917823944","‐0,0917823944","‐0,0917823944","‐0,0917823944","‐0,0917823944","‐0,0917823944","‐0,0917823944",null,null,"Corrección perdidas circuito primario"]
[null,"Ln F3",null,"‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ","‐0,0091913509 ",null,null,"Total perdida térmica",{"v":1134.307020581792,"d":"1134"},"W"]
[null,"Ln A9",null,0.0546786339,0.0546786339,0.0546786339,0.0546786339,0.0546786339,0.0546786339,0.0546786339,0.0546786339,0.0546786339,0.0546786339,0.0546786339,0.0546786339,0.0546786339,null,null,"Salto termico",{"v":40,"d":"40.00"}]
[null,"F1 x F2",null,"‐0,1494371856","‐0,1494371856","‐0,1494371856","‐0,1494371856","‐0,1494371856","‐0,1494371856","‐0,1494371856","‐0,1494371856","‐0,1494371856","‐0,1494371856","‐0,1494371856","‐0,1494371856","‐0,1494371856",null,null,"UA",{"v":18.905117009696532,"d":"18.91"},"W/K"]
[{"$nulls":18},"sup absorvedor panel",2.352]
[null,1,null,"‐0,7355038529 ",{"$nulls":14},"nº paneles",14]
[null,"Ln F1",null,6.896171418885712,{"$nulls":14},"A2",32.928]
[null,"Ln A3",null,{"$error":"#REF!"},{"$nulls":14},"numerador",0.9968980850352067,null,0.4835300496609578]
[null,"A2/A3",null,{"$error":"#REF!"},{"$nulls":14},"denominador",1.0031019149647933]
[null,"A1",null,0,{"$nulls":13},">>>","f UL",{"v":0.9938153543154143,"d":"0.99"},"Corrige las perdidas en primario"]
[null,"A5",null,{"$error":"#N/A"}]
[null,"A4",null,0,{"$nulls":14},"numerador",1]
[null,"X2",null,{"$error":"#VALUE!"},{"$nulls":14},"denominador",1.0031019149647933]
[null,"X3",null,{"$error":"#REF!"},{"$nulls":13},">>>","f alfa",{"v":0.9969076771577072,"d":"1.00"}]
[null,"X4",null,{"$error":"#VALUE!"}]
[null,"Ln A6",{"$nulls":16},"Corrección efectividad intercambiador de placas"]
[null,"LnA7",{"$nulls":16},"Efectividad inter. Placas","0,970"]
[null,"Ln A8",{"$nulls":15},">>>","f UL","0,970"]
[null,"Ln F3"]
[null,"Ln A9",{"$nulls":16},"VALORES TOTALES"]
[null,"F1 x F2",{"$nulls":17},"inicial","FR","r primario","f serie","K primario","f placas","TOTAL","factor"]
[{"$nulls":18},"A0",0.79,{"v":0.9837059247918836,"d":"0.98"},{"v":1.0012000697185506,"d":"1.00"},{"v":1,"d":"1.00"},{"v":0.9969076771577072,"d":"1.00"},{"v":1,"d":"1.00"},{"v":0.7756542743812971,"d":"0.78"},{"v":0.9818408536472114,"d":"0.98"}]
[null,"Ln(Y)",null,{"$error":"#REF!"},{"$nulls":14},"A1",{"v":2.4141,"d":"2.41"},{"v":0.9837059247918836,"d":"0.98"},{"v":1.0012000697185506,"d":"1.00"},{"v":1,"d":"1.00"},{"v":0.9968980850352067,"d":"1.00"},"0,970",{"v":2.2991320224689242,"d":"2.30"},{"v":0.9523764643009504,"d":"0.95"}]
[null,"Y1",null,{"$error":"#REF!"}]
[null,"Y7",null,40]
[null,"Y2",null,{"$error":"#REF!"}]
[null,"Fraccion",null,{"$error":"#REF!"}]
[]
[]
[]
[]
[null,null,"problemas f chart"]

{"sheet":"Perdidas","index":3,"n_rows":35,"n_cols":26,"rows_kept":35,"hidden":true,"merged":[[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,14,3,15]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":1}
[]
[null,"Esquema","Colectivo Inter-acumulador central",{"$nulls":14},"Sin pérdidas térmicas",null,null,"Sin pérdidas térmicas"]
[{"$nulls":17},"Estimación SIMPLIFICADA",null,null,"Estimadas según CLASE ENERGÉTICA"]
[null,"Circuito","Primario",null,"Carga inercia",null,"Decarga inercia",null,"Secundario",null,"Consumo",null,"Distribución",null,"Retorno",null,null,"Estimación por CIRCUITOS",null,null,"Perdidas según FICHA Epr"]
[null,null,"interior","exterior","interior","exterior","interior","exterior","interior","exterior","interior","exterior","interior","exterior","interior","exterior",{"$nulls":4},"Estimadas según AISLAMIENTO"]
[]
[null,"Horas/dia",6,6,6,6,6,6,6,6,12,12,24,24,24,24,null,"Perdidas acumulador"]
[null,"Tª circuito",60,60,55,55,50,50,45,45,60,60,55,55,50,50]
[{"$nulls":18},"A","B","C","D","E","F","G"]
[{"$nulls":16},1,6000,127,175,246,322,413,520,572]
[{"$nulls":16},2,5000,119,164,229,300,385,486,534]
[{"$nulls":16},3,4000,109,151,211,276,354,447,491]
[{"$nulls":16},4,3000,98,135,190,248,319,401,441]
[{"$nulls":16},5,2000,84,117,163,214,274,346,379]
[{"$nulls":16},6,1000,66,91,127,167,214,269,295]
[{"$nulls":16},7,800,61,84,118,154,197,248,272]
[{"$nulls":16},8,500,52,71,100,131,168,211,231]
[{"$nulls":16},9,300,43,60,84,110,141,177,194]
[{"$nulls":16},10,200,38,53,74,97,123,155,170]
[{"$nulls":16},11,150,34,48,67,88,113,141,155]
[{"$nulls":16},12,100,30,42,59,78,99,124,136]
[]
[]
[]
[]
[]
[{"$nulls":24},"Clase","C"]
[{"$nulls":17},"Acumuladores","A","B","C","D","E","F","G"]
[{"$nulls":16},5,2000,84,117,163,214,274,346,379,163]
[{"$nulls":16},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"},{"$error":"#DIV/0!"}]
[]
[]
[{"$nulls":17},"busqueda según clase",null,"W"]
[{"$nulls":15},"acumulador 1","B",2000,2,117]
[{"$nulls":15},"acumulador 2",{"v":0,"d":"0.00"},0,{"$error":"#N/A"},0]

{"sheet":"Datos CTE","index":4,"n_rows":104,"n_cols":18,"rows_kept":104,"hidden":true,"merged":[[3,1,3,3],[28,1,28,3],[39,1,39,3],[45,1,45,3],[50,1,50,3],[59,1,59,3],[66,1,66,3],[72,1,72,3],[90,1,90,3],[91,4,91,5],[91,6,91,7],[91,8,91,9],[91,10,91,11],[91,12,91,13],[91,14,91,15],[91,16,91,17]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":1}
[]
[null,"DATOS CTE  HE-4     CONTRIBUCIÓN SOLAR MÍNIMA"]
[]
[null,"Consumo acs a 60ºC   CTE HE4 2013 Tabla 3,1"]
[null,"Viviendas",28,"Nº de personas:","nº"]
[null,"Sin otros usos",0]
[null,"Hospitales y clinicas",55,"Nº de personas:","nº"]
[null,"Ambukatorios / Centros salud",41]
[null,"Hoteles 5 ****",69,"Nº de personas:","nº"]
[null,"Hoteles 4 ****",55,"Nº de personas:","nº"]
[null,"Hotel 3 ***",41,"Nº de personas:","nº"]
[null,"Hotel / Hostal 2 **",34,"Nº de personas:","nº"]
[null,"Camping",21,"Nº de personas:","nº"]
[null,"Hostal / Pensión 1 *",28,"Nº de personas:","nº"]
[null,"Residencia publica",41,"Nº de personas:","nº"]
[null,"Centro penitenciario",28,"Nº de personas:","nº"]
[null,"Albergue",24,"Nº de personas:","nº"]
[null,"Vestuarios/duchas colectivas",21,"Nº de personas:","nº"]
[null,"Escuelas sin duchas",4,"Nº de personas:","nº"]
[null,"Escuelas con duchas",21,"Nº de personas:","nº"]
[null,"Cuarteles",28,"Nº de personas:","nº"]
[null,"Fábricas y talleres",21,"Nº de personas:","nº"]
[null,"Administrativos",2,"Nº de personas:","nº"]
[null,"Gimnasios",21,"Nº de personas:","nº"]
[null,"Restaurantes",8,"Nº de personas:","nº"]
[null,"Cafeterías",1,"Nº de personas:","nº"]
[null,"Otros (1 l/d por persona)",1,"Demanda de litros ACS/día a 60ºC","l/d"]
[]
[null,"Contribución solar mínima  CTE HE4 Tabla 2.1"]
[]
[null,"Zona climática","IV",null,"fila",1]
[null,"Vol. Acumulación",1612.8,null,"columna",4]
[null,"%min solar",{"v":0.6,"d":"60.00%"}]
[]
[null,"min","max",null,"I","II","III","IV","V"]
[null,50,{"v":5000,"d":"5,000"},null,{"v":0.6,"d":"60.00%"},{"v":0.6,"d":"60.00%"},{"v":0.6,"d":"60.00%"},{"v":0.6,"d":"60.00%"},{"v":0.6,"d":"60.00%"}]
[null,{"v":5001,"d":"5,001"},{"v":10000,"d":"10,000"},null,{"v":0.7,"d":"70.00%"},{"v":0.7,"d":"70.00%"},{"v":0.7,"d":"70.00%"},{"v":0.7,"d":"70.00%"},{"v":0.7,"d":"70.00%"}]
[null,{"v":10001,"d":"10,001"},null,null,{"v":0.7,"d":"70.00%"},{"v":0.7,"d":"70.00%"},{"v":0.7,"d":"70.00%"},{"v":0.7,"d":"70.00%"},{"v":0.7,"d":"70.00%"}]
[]
[null,"Pérdidas Límite   CTE HE4 Tabla 2.4"]
[{"$nulls":3},"Orientación e inclinación","Sombras","Total"]
[1,"General",null,{"v":0.1,"d":"10.00%"},{"v":0.1,"d":"10.00%"},{"v":0.15,"d":"15.00%"}]
[2,"Superposición",null,{"v":0.2,"d":"20.00%"},{"v":0.15,"d":"15.00%"},{"v":0.3,"d":"30.00%"}]
[3,"Integración",null,{"v":0.4,"d":"40.00%"},{"v":0.2,"d":"20.00%"},{"v":0.5,"d":"50.00%"}]
[]
[null,"Calculo de ocupación en uso residencial vivienda"]
[{"$nulls":3},"nº Dormitorios",1,2,3,4,5,6,7,">7"]
[]
[{"$nulls":3},"Nº Ocupantes (2013)",1.5,3,4,5,6,6,7,7]
[]
[null,"Factor de centralización"]
[{"$nulls":4},"limites","factor"]
[null,"nº viviendas",16,null,3,1]
[null,"fila",3,null,4,0.95]
[null,"factor",0.9,null,11,0.9]
[{"$nulls":4},21,0.85]
[{"$nulls":4},51,0.8]
[{"$nulls":4},76,0.75]
[{"$nulls":4},101,0.7]
[null,"Zona radiación solar"]
[]
[null,"Radiación global anual",{"v":17.593376,"d":"17.59"},"MJ/m2 dia","I",{"v":0,"d":"0.00"},{"v":13.6999999999999,"d":"13.70"}]
[null,"fila",{"v":4,"d":"4.00"},null,"II",{"v":13.7,"d":"13.70"},{"v":15.0999999999999,"d":"15.10"}]
[null,"Zona radiación","IV",null,"III",{"v":15.1,"d":"15.10"},{"v":16.5999999999999,"d":"16.60"}]
[{"$nulls":4},"IV",{"v":16.6,"d":"16.60"},{"v":17.9999999999999,"d":"18.00"}]
[{"$nulls":4},"V",{"v":18,"d":"18.00"},{"v":100000,"d":"100000.00"}]
[null,"Equipos de apoyo"]
[]
[null,"Combustion "]
[null,"Electrico (Joule)"]
[]
[]
[null,"Equipos de apoyo"]
[{"$nulls":15},"EP tot","EP nr","EP rn"]
[null,"Según equipo",null,null,"EP total","EP nr","EP r",null,"Electricidad","EP total","EP nr","EP r",null,null,"combustible",1.195,1.19,0.0050000000000001155]
[null,"Gas natural",null,"Gas natural",1.195,1.19,0.0050000000000001155,null,"Palmas de Gran Canarias",2.994,2.924,0.07000000000000028,null,null,"electricidad",2.368,1.964,0.4039999999999999]
[null,"Gasoleo",null,"Gasoleo",1.182,1.179,0.0029999999999998916,null,"Santa Cruz de Tenerife",2.994,2.924,0.07000000000000028]
[null,"GLP",null,"GLP",1.204,1.201,0.0029999999999998916,null,"Palma de Mallorca",3.049,2.968,0.08099999999999996]
[null,"Biomasa (pellet)",null,"Biomasa (pellet)",1.113,0.085,1.028,null,"Ceuta",2.79,2.718,0.07200000000000006]
[null,"Biomasa (no densif.)",null,"Biomasa (no densif.)",1.037,0.034,1.003,null,"Melilla",2.79,2.718,0.07200000000000006]
[{"$nulls":3},"Electricidad",2.368,1.964,0.4039999999999999,null,"Peninsular",2.368,1.964,0.4039999999999999]
[]
[null,"Gas natural","EP tot",1.195,{"$nulls":4},6,2.368,1.964,0.4039999999999999]
[null,null,"EP nr",1.19]
[null,null,"EP rn",0.0050000000000001155]
[]
[null,"Combustion "]
[null,0.95]
[]
[]
[null,"Tipo de sistemas"]
[null,"esquemas","selec:","Colectivo Inter-acumulador central","Primario",null,"Carga inercia",null,"Decarga inercia",null,"Secundario",null,"Consumo",null,"Distribución",null,"Retorno"]
[{"$nulls":4},"interior","exterior","interior","exterior","interior","exterior","interior","exterior","interior","exterior","interior","exterior","interior","exterior"]
[{"$nulls":3},"Individual con Inter-acumulador",1,1,0,0,0,0,0,0,1,1,1,1,1,1]
[{"$nulls":3},"Individual con Intercambiador",1,1,0,0,0,0,1,1,1,1,1,1,1,1]
[]
[{"$nulls":3},"Individual compacto Termosifón",1,1,0,0,0,0,0,0,1,1,1,1,1,1]
[{"$nulls":3},"Individual compacto Drain Back",1,1,0,0,0,0,0,0,1,1,1,1,1,1]
[]
[{"$nulls":3},"Colectivo Inter-acumulador central",1,1,0,0,0,0,0,0,1,1,1,1,1,1]
[{"$nulls":3},"Colectivo Intercambiador central",1,1,0,0,0,0,1,1,1,1,1,1,1,1]
[{"$nulls":3},"Colectivo ACS Centralizada",1,1,0,0,0,0,1,1,1,1,1,1,1,1]
[{"$nulls":3},"Colectivo Acumulacion distribuida",1,1,0,0,0,0,0,0,1,1,1,1,1,1]
[{"$nulls":3},"Colectivo Intercambio distribuido",1,1,0,0,0,0,1,1,1,1,1,1,1,1]

{"sheet":"Sombras","index":5,"n_rows":84,"n_cols":40,"rows_kept":84,"merged":[[1,1,1,2],[1,3,1,5],[1,20,1,24],[2,1,2,2],[2,3,2,5],[2,20,2,24],[3,1,3,2],[3,3,3,5],[4,20,4,21],[4,23,4,24],[5,1,5,4],[5,20,5,21],[5,23,5,24],[8,2,19,4],[22,1,22,5],[23,1,25,5],[25,20,25,22],[25,23,25,24],[26,1,26,5],[28,1,28,5],[28,20,28,22],[29,1,29,5],[29,20,29,22],[31,13,31,14],[31,16,31,17],[33,7,49,11],[33,20,40,24],[42,1,42,2],[42,4,42,5],[43,4,43,5],[51,1,51,5],[51,7,51,11]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":3}
[]
[null,"Localidad",null,"Madrid",{"$nulls":16},"PERFILES ADICIONALES DE OBSTRUCCION SOLAR"]
[null,"Latitud",null,{"v":40.4,"d":"40.40"},{"$nulls":16},"(No referenciados a la posición del panel)",{"$nulls":4},-2.588190451025208,0,null,"Perfil edificio"]
[null,"Datos Radiación",null,"Atlas Radiacion solar 2012 AEMET"]
[{"$nulls":20},"Grupo 1",null,null,"Grupo 2",null,-9.659258262890683,0,null,"Proteccion solar"]
[null,"Orientación de los captadores (Azimut)",{"$nulls":3},15,{"$nulls":14},"Perfil edificio",null,null,"Perfil edificio"]
[{"$nulls":25},105,90,null,true,null,null,true,{"$nulls":3},false,0,null,false,0]
[{"$nulls":20},"azimut","altura",null,"azimut","altura",105,0,{"$nulls":8},"azimut","altura",null,"azimut","altura"]
[{"$nulls":20},90,20,null,-90,45,{"$nulls":3},90,20,null,-90,45,null,null,0,0,null,0,0]
[{"$nulls":20},115,30,null,-50,40,-75,90,null,115,30,null,-50,40,null,null,0,0,null,0,0]
[{"$nulls":20},{"v":115,"d":"115.00"},{"v":0,"d":"0.00"},null,{"v":-50,"d":"-50.00"},{"v":0,"d":"0.00"},-75,0,null,115,0,null,-50,0,null,null,0,0,null,0,0]
[{"$nulls":20},{"v":90,"d":"90.00"},{"v":0,"d":"0.00"},null,{"v":-90,"d":"-90.00"},{"v":0,"d":"0.00"},{"$nulls":3},90,0,null,-90,0,null,null,0,0,null,0,0]
[{"$nulls":20},90,20,null,-90,45,{"$nulls":10},0,0,null,0,0]
[{"$nulls":20},"azimut","altura",null,"azimut","altura",-9.659258262890685,0,{"$nulls":8},"azimut","altura",null,"azimut","altura"]
[{"$nulls":20},115,30,null,-90,45,2.588190451025203,0,null,115,30,null,-90,45,null,null,0,0,null,0,0]
[{"$nulls":20},120,20,null,-120,65,{"$nulls":3},120,20,null,-120,65,null,null,0,0,null,0,0]
[{"$nulls":20},{"v":120,"d":"120.00"},{"v":0,"d":"0.00"},null,{"v":-120,"d":"-120.00"},{"v":0,"d":"0.00"},9.659258262890683,0,null,120,0,null,-120,0,null,null,0,0,null,0,0]
[{"$nulls":20},{"v":115,"d":"115.00"},{"v":0,"d":"0.00"},null,{"v":-90,"d":"-90.00"},{"v":0,"d":"0.00"},-2.588190451025229,0,null,115,0,null,-90,0,null,null,0,0,null,0,0]
[{"$nulls":20},115,30,null,-90,45,{"$nulls":10},0,0,null,0,0]
[{"$nulls":20},"azimut","altura",null,"azimut","altura",210,90,{"$nulls":8},"azimut","altura",null,"azimut","altura"]
[{"$nulls":20},90,20,null,-120,65,210,0,null,90,20,null,-120,65,null,null,0,0,null,0,0]
[null,null,195,{"$nulls":17},25,15,null,-180,60,-180,90,null,25,15,null,-180,60,null,null,0,0,null,0,0]
[null,"Actualizaciones y otras herramientas en:",{"$nulls":18},{"v":25,"d":"25.00"},{"v":0,"d":"0.00"},null,{"v":-180,"d":"-180.00"},{"v":0,"d":"0.00"},-180,0,null,25,0,null,-180,0,null,null,0,0,null,0,0]
[{"$nulls":20},{"v":90,"d":"90.00"},{"v":0,"d":"0.00"},null,{"v":-120,"d":"-120.00"},{"v":0,"d":"0.00"},{"$nulls":3},90,0,null,-120,0,null,null,0,0,null,0,0]
[{"$nulls":20},90,20,null,-120,65,{"$nulls":10},0,0,null,0,0]
[{"$nulls":20},"Inclinación de los captadores",null,null,{"v":40,"d":"40.00 grados"},null,{"v":9045.043020116778,"d":"9,045"}]
[null,"Autor: Oscar Redondo Rivera.       o.redondo.rivera@gmail.com"]
[{"$nulls":7},"Ene","Feb","Mar","Abr","May","Jun","Jul","Ago","Sep","Oct","Nov","Dic",{"$nulls":4},"directa","global"]
[null,"% Obstruccion sobre radiación DIRECTA",{"$nulls":5},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},null,"% Obstruccion solar INVIERNO",null,null,{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"}]
[null,"% Obstruccion sobre radiación GLOBAL",{"$nulls":5},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},null,"% Obstruccion solar VERANO",null,null,{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},null,0,{"$nulls":3},false,0,{"$nulls":4},false,0,false,0]
[{"$nulls":28},false]
[null,null,"PETO DE CUBIERTA PLANA",{"$nulls":5},"OBSTACULOS EN CUBIERTA",{"$nulls":4},"Obstáculo 1",null,null,"Obstáculo 2",{"$nulls":4},"OBSTACULO SUPERIOR"]
[{"$nulls":25},true,1,null,true,1,null,true,1,false,0,true]
[{"$nulls":13},"Alfa 1",0,null,"Alfa 1",25]
[{"$nulls":13},"dist 1",4,null,"dist 1",5]
[]
[{"$nulls":13},"Alfa 2",25,null,"Alfa 2",50]
[{"$nulls":13},"dist 2",5,null,"dist 2",10]
[]
[{"$nulls":13},"Alfa 3",-25,null,"Alfa 3",0]
[{"$nulls":13},"dist 3",5,null,"dist 3",10]
[]
[null,"Geometría ",null,null,"Incluir laterales"]
[{"$nulls":4},"SI",{"$nulls":8},"Altura ",3,null,"Altura ",5]
[null,"a",5,"m",{"$nulls":16},"a",3,null,"c",1,null,"SI"]
[null,"b",5,"m",{"$nulls":16},"b",3,null,"h",2,null,"NO"]
[null,"c",10,"m"]
[]
[null,"h",1,"m"]
[]
[null,"β",15,"º",{"$nulls":14},1]
[null,0]
[{"$nulls":4},"azimut","altura","d",null,null,"azimut","altura","d",{"$nulls":3},"azimut","altura","d",{"$nulls":4},"azimut","altura"]
[null,null,"Frontal 1",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},3.8366349398948016,"Saliente 1",1,0,0,0,null,"Obtáculo 1",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},4,null,null,"Alero a",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},3.1622776601683795]
[null,null,"Der",2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},5,null,2,0,0,0,null,null,2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},5,{"$nulls":3},2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":3},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},null,null,3,0,0,{"$nulls":3},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":4},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":3},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},null,null,4,0,0,{"$nulls":3},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":4},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":4},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":3},0,0,{"$nulls":4},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":5},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,null,"Frontal 2",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},3.8366349398948016,"Saliente 2",1,0,0,0,null,"Obtáculo 1",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":3},"Alero b",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},3.1622776601683795]
[null,null,"Izq",2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},null,null,2,0,0,0,null,null,2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},5,{"$nulls":3},2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":3},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},null,null,3,0,0,{"$nulls":3},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":4},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":3},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},null,null,4,0,0,{"$nulls":3},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":4},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":4},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":3},0,0,{"$nulls":4},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":5},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,null,"Lateral Der",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":7},"Obtáculo 2",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},5,null,null,"Lateral a",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":3},2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},-1.852952387243698,{"$nulls":7},2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},10,{"$nulls":3},2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":3},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":8},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":4},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":3},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":8},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":4},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":4},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":9},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":5},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,null,"Lateral Izq",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":7},"Obtáculo 2",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},5,null,null,"Lateral b",1,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":3},2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},1.852952387243698,{"$nulls":7},2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},10,{"$nulls":3},2,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":3},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":8},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":4},3,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":3},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":8},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"$nulls":4},4,{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[{"$nulls":4},0,0,{"$nulls":9},0,0,{"$nulls":5},0,0]
[{"$nulls":5},1,{"$nulls":7},"Obtáculo 3",1,0,0,5]
[{"$nulls":3},"x","y",{"$nulls":8},"Frontal ",2,0,0,0]
[null,null,"fachada",0,5,{"$nulls":9},3,0,0]
[{"$nulls":3},10,5,{"$nulls":9},4,0,0]
[null,null,"lat der",10,5,{"$nulls":10},0,0]
[{"$nulls":3},10,0,{"$nulls":8},"Obtáculo 3",1,0,0]
[null,null,"lat izq",0,5,{"$nulls":8},"Lateral",2,0,0,0]
[{"$nulls":3},0,0,{"$nulls":9},3,0,0]
[null,null,"Frontal",0,0,{"$nulls":9},4,0,0]
[{"$nulls":3},10,0,{"$nulls":10},0,0]
[null,null,"Ref",5,5]

{"sheet":"Tablas primario","index":6,"n_rows":14,"n_cols":10,"rows_kept":14,"hidden":true,"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":1}
[]
[null,"Tuberia de cobre sanitario"]
[null,"Dim. Ext","Dim int.","espesor","Volumen"]
[null,"(mm)","(mm)","(mm)","(litros/ml)",null,"cobre",560,null,"paralelo"]
[1,"15/13",13,{"v":1,"d":"1.00"},{"v":0.13273228961416877,"d":"0.133"},null,"acero inox.",700,null,"serie"]
[2,"18/16",16,{"v":1,"d":"1.00"},{"v":0.20106192982974674,"d":"0.201"}]
[3,"22/20",20,{"v":1,"d":"1.00"},{"v":0.3141592653589793,"d":"0.314"},null,"agua",{"v":1,"d":"1.00"}]
[4,"28/26",{"v":25.6,"d":"26"},{"v":1.2,"d":"1.20"},{"v":0.5147185403641518,"d":"0.515"},null,"agua glicolada",{"v":1.3,"d":"1.30"}]
[5,"35/33",{"v":32.6,"d":"33"},{"v":1.2,"d":"1.20"},{"v":0.8346897521322723,"d":"0.835"}]
[6,"42/40",{"v":39.6,"d":"40"},{"v":1.2,"d":"1.20"},{"v":1.2316299839133424,"d":"1.232"}]
[7,"54/52",{"v":51.6,"d":"52"},{"v":1.2,"d":"1.20"},{"v":2.09116973393551,"d":"2.091"}]
[]
[null,"Acumulación centralizada"]
[null,"Acumulación individual"]

{"sheet":"Informe calculo","index":7,"n_rows":127,"n_cols":18,"rows_kept":127,"merged":[[1,1,1,16],[2,1,2,16],[4,3,4,13],[4,14,4,15],[6,3,6,6],[6,8,6,11],[7,8,7,11],[7,12,7,15],[8,8,8,11],[8,12,8,15],[9,12,9,15],[11,3,11,16],[12,3,12,16],[13,3,13,16],[15,1,15,16],[31,1,31,16],[42,3,42,5],[47,6,47,7],[52,1,52,16],[58,5,58,6],[58,16,71,16],[60,3,60,6],[73,1,73,16],[75,5,75,15],[99,8,99,16],[103,8,103,10],[103,11,103,12],[104,8,104,10],[104,11,104,12],[108,8,108,10],[108,11,108,12],[109,8,109,10],[109,11,109,12],[113,8,113,10],[113,11,113,12],[114,8,114,10],[114,11,114,12],[116,8,116,10],[116,11,116,12],[117,8,117,10],[117,11,117,12],[118,8,118,10],[118,11,118,12],[119,8,119,10],[119,11,119,12]],"flags":["formulas_cached_only"]}
[]
[null,"INSTALACIÓN SOLAR TÉRMICA"]
[null,"Informe de calculo de cumplimiento del CTE-HE4"]
[]
[null,"PROYECTO",null,"Ejemplo",{"$nulls":10},"Cumple CTE",null,"CUMPLE",1]
[]
[null,"Localidad",null,"Madrid",{"$nulls":4},"Tipo de sistema solar",{"$nulls":3},"Colectivo Inter-acumulador central"]
[null,"Zona climática s/ CTE-HE4",null,"IV",{"$nulls":4},"Tipo de sistema de apoyo",{"$nulls":3},"Combustion "]
[null,"Zona Climática s/ CTE-HE1",null,"D3",{"$nulls":4},"Combustible sistema de apoyo",{"$nulls":3},"Gas natural"]
[null,"Latitud de cálculo:",null,40.4,null,"altura",{"v":655,"d":"655 m"},null,"Rendimiento sistema de apoyo",{"$nulls":3},0.95]
[]
[null,"Método de calculo",null,"Método f-chart según documento reconocido ASIT - IDAE"]
[null,"Datos de radiación solar",null,"Atlas Radiacion solar 2012 AEMET"]
[null,"Datos de Tª del agua",null,"Anexo B del CTE-HE4 2013 para la localidad del edificio"]
[]
[null,"CALCULO DE NECESIDADES DE ACS"]
[]
[null,"Demanda de ACS viviendas",null,{"v":1612.8,"d":"1,613"},"litros/dia"]
[null,"Demanda de ACS otros usos",null,0,"litros/dia"]
[]
[null,"Demanda TOTAL de ACS a 60ºC",null,{"v":1612.8,"d":"1,613"},"litros/dia"]
[]
[null,"Temperatura de agua en calculo",null,60,"ºC"]
[null,"Demanda TOTAL de ACS a 60ºC",null,{"v":1612.8,"d":"1,613"},"litros/dia"]
[]
[{"$nulls":3},"Ene","Feb","Mar","Abr","May","Jun","Jul","Ago","Sep","Oct","Nov","Dic","Anual"]
[null,"% ocupación prevista",null,{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"},{"v":1,"d":"100.00%"}]
[null,"Consumo mensual de agua  (l/mes)",null,{"v":49996.799999999996,"d":"49,997"},{"v":45158.4,"d":"45,158"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":48384,"d":"48,384"},{"v":49996.799999999996,"d":"49,997"},{"v":588672,"d":"588,672"}]
[]
[null,"Demanda TOTAL de ACS a 60ºC",null,{"v":1612.8,"d":"1,613"},"litros/dia"]
[]
[null,"EQUIPOS SELECCIONADOS"]
[]
[null,"Volumen de acumulación proyectado",null,{"v":2000,"d":"2,000"},"litros"]
[null,"Nº de depositos",null,{"v":1,"d":"1 Ud x"},"SD Acumulador BDLE 2000"]
[{"$nulls":3},"",""]
[]
[null,"Panel solar proyectado",null,{"v":14,"d":"14 Ud x"},"Saunier Duval"]
[null,"Factores de rendimiento del panel",null,"a0",{"v":0.79,"d":"0.790"},"a1",{"v":2.4141,"d":"2.414"},"a2",0.049]
[null,"Número de grupos",null,2]
[null,"Número de paneles por grupo",null,7]
[]
[null,"Sistema de disipación de calor",null,"Sistema Drain-Back",{"$nulls":3},"Potencia",{"v":32,"d":"32.00 kW"}]
[]
[null,"Superficie de captación del panel (m²)",null,{"v":2.352,"d":"2.35"},"m2"]
[]
[null,"Area total de captación proyectada (m2)",null,{"v":32.928,"d":"32.93"},"m2"]
[null,"Relación Volumen/área captación",null,{"v":60.738581146744416,"d":"60.74"},"Valor entre 50 y 180",null,"CUMPLE",null,1]
[]
[null,"Orientación de los captadores",null,15,"grados respecto al Sur"]
[null,"Inclinación de los captadores",null,40,"grados de inclinación"]
[]
[null,"CUMPLIMIENTO DEL CTE HE4"]
[]
[{"$nulls":3},"Ene","Feb","Mar","Abr","May","Jun","Jul","Ago","Sep","Oct","Nov","Dic",null,"Anual"]
[null,"% demanda neta aportada por el sistema solar",null,{"v":0.30300361787342067,"d":"30.30%"},{"v":0.4640643912761879,"d":"46.41%"},{"v":0.6338774980388323,"d":"63.39%"},{"v":0.7153523066065581,"d":"71.54%"},{"v":0.7681160406471582,"d":"76.81%"},{"v":0.8777936280434953,"d":"87.78%"},{"v":0.9405594418575782,"d":"94.06%"},{"v":0.9151986134503998,"d":"91.52%"},{"v":0.8304987243104468,"d":"83.05%"},{"v":0.6051178385898652,"d":"60.51%"},{"v":0.39287638387983403,"d":"39.29%"},{"v":0.24019541573543163,"d":"24.02%"},null,{"v":0.6219928289834757,"d":"62.20%"}]
[]
[{"$nulls":3},"Mínimo","Proyectado"]
[null,"Contribución anual del sistema",null,{"v":0.6,"d":"60%"},{"v":0.6219928289834757,"d":"62.20%"},"CUMPLE",null,1]
[]
[null,"Disposición del modulo solar",null,"Superposición"]
[]
[{"$nulls":3},"Maximo","Proyectado"]
[null,"Perdidas por orientación e inclinación",null,{"v":0.2,"d":"20%"},{"v":0.0078942,"d":"0.79%"},null,null,0]
[null,"Perdida límite por sombras",null,{"v":0.15,"d":"15%"},{"v":0,"d":"0.00%"},null,null,0]
[null,"Perdida límite TOTAL",null,{"v":0.3,"d":"30%"},{"v":0.0078942,"d":"0.79%"},null,null,0]
[]
[null,"Ningún mes supera una contribucion del 110%",null,"max",{"v":0.9405594418575782,"d":"94.06%"},null,null,1]
[null,"< 100% de contribución en más de 3 meses seguidos",{"$nulls":5},1]
[]
[null,"Demanda de energía convencional",null,{"v":12124.133248215676,"d":"12,124"},"kWh/año"]
[null,"Porcentaje de uso de energía convencional",null,{"v":0.37800717101652426,"d":"37.80%"}]
[]
[null,"CALCULO DE LA APORTACIÓN POR EL MÉTODO F-CHART"]
[]
[null,"Estimación perdidas térmicas del circuito y acumulación",null,{"v":0.1,"d":"10.00%"},null,"Ecuación de la fracción de carga calorífica mensual aportada:  f = 1,029D1 - 0,065D2 - 0,245D1² + 0,0018D2² + 0,215D1³"]
[]
[null,"DEMANDA NETA DE ACS",null,"Ene","Feb","Mar","Abr","May","Jun","Jul","Ago","Sep","Oct","Nov","Dic","Anual"]
[null,"(DEacs)  Demanda neta de ACS (kWh)",null,{"v":3015.8069759999994,"d":"3,016"},{"v":2723.9546880000003,"d":"2,724"},{"v":2899.8144,"d":"2,900"},{"v":2694.02112,"d":"2,694"},{"v":2667.829248,"d":"2,668"},{"v":2413.39392,"d":"2,413"},{"v":2319.8515199999997,"d":"2,320"},{"v":2377.847808,"d":"2,378"},{"v":2413.39392,"d":"2,413"},{"v":2725.8255359999994,"d":"2,726"},{"v":2806.272,"d":"2,806"},{"v":3015.8069759999994,"d":"3,016"},{"v":32073.818111999997,"d":"32,074"},"kWh/mes"]
[]
[null,"ENERGIA ABSORBIDA POR CAPTADORES",null,"Ene","Feb","Mar","Abr","May","Jun","Jul","Ago","Sep","Oct","Nov","Dic","Anual"]
[null,"Factor de corrección por inclinación (k)",null,1.39,1.29,1.16,1.04,0.95,0.92,0.95,1.05,1.21,1.39,{"v":1.5,"d":"1.50"},1.48,{"v":1.1941666666666668,"d":"1.19"}]
[null,"Factor de corrección por orientación",null,{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.992125,"d":"0.99"},{"v":0.9921249999999998,"d":"0.99"}]
[null,"Factor de corrección por sombras ",null,{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"}]
[null,"Factor de corección total",null,{"v":1.37905375,"d":"1.38"},{"v":1.27984125,"d":"1.28"},{"v":1.150865,"d":"1.15"},{"v":1.0318100000000001,"d":"1.03"},{"v":0.94251875,"d":"0.94"},{"v":0.9127550000000001,"d":"0.91"},{"v":0.94251875,"d":"0.94"},{"v":1.04173125,"d":"1.04"},{"v":1.20047125,"d":"1.20"},{"v":1.37905375,"d":"1.38"},{"v":1.4881875,"d":"1.49"},{"v":1.468345,"d":"1.47"},{"v":1.1847626041666668,"d":"1.18"}]
[null,"Radiación solar incidente (KWh/m² mes)",null,{"v":97.18418707205971,"d":"97"},{"v":116.63378177208334,"d":"117"},{"v":166.13681902408334,"d":"166"},{"v":178.24431765833336,"d":"178"},{"v":193.11788195791664,"d":"193"},{"v":212.24784902700003,"d":"212"},{"v":235.25269256691658,"d":"235"},{"v":226.38220612291667,"d":"226"},{"v":197.28188382695836,"d":"197"},{"v":152.41220527600555,"d":"152"},{"v":108.64557489375,"d":"109"},{"v":85.24291070282779,"d":"85"},{"v":1968.7823099008515,"d":"1,969"},"KWh/m² mes"]
[null,"Radiación solar absorvida (KWh/mes)",null,{"v":2135.9934109430437,"d":"2,136"},{"v":2563.4724831707017,"d":"2,563"},{"v":3651.490653385345,"d":"3,651"},{"v":3917.599143716023,"d":"3,918"},{"v":4244.502483634799,"d":"4,245"},{"v":4664.956518824925,"d":"4,665"},{"v":5170.575752791482,"d":"5,171"},{"v":4975.612959284814,"d":"4,976"},{"v":4336.022316473786,"d":"4,336"},{"v":3349.8398867653027,"d":"3,350"},{"v":2387.9011503085117,"d":"2,388"},{"v":1873.5382892675718,"d":"1,874"},{"v":43271.5050485663,"d":"43,272"},"KWh/mes"]
[]
[null,"CALCULO APORTE SOLAR NETO",null,"Ene","Feb","Mar","Abr","May","Jun","Jul","Ago","Sep","Oct","Nov","Dic","Anual"]
[null,"Relación  radiación absorvida y ener. demandada",null,{"v":0.7082659559916888,"d":"0.71"},{"v":0.9410848478734686,"d":"0.94"},{"v":1.259215297842974,"d":"1.26"},{"v":1.4541827881869103,"d":"1.45"},{"v":1.590994808538361,"d":"1.59"},{"v":1.9329445061438313,"d":"1.93"},{"v":2.2288390908705584,"d":"2.23"},{"v":2.0924858784254092,"d":"2.09"},{"v":1.796649225201407,"d":"1.80"},{"v":1.228926738899442,"d":"1.23"},{"v":0.8509157880307082,"d":"0.85"},{"v":0.6212394573582856,"d":"0.62"},{"v":1.349122355731538,"d":"1.35"},"valor Yi"]
[null,"Factor de corrección por consumo Tª ACS",null,{"v":1.054328358208955,"d":"1.05"},{"v":1.03792656587473,"d":"1.04"},{"v":1.0880355160932298,"d":"1.09"},{"v":1.1436902050113895,"d":"1.14"},{"v":1.1823809523809523,"d":"1.18"},{"v":1.260983606557377,"d":"1.26"},{"v":1.3623280423280424,"d":"1.36"},{"v":1.3178975032851514,"d":"1.32"},{"v":1.2636477987421382,"d":"1.26"},{"v":1.154466588511137,"d":"1.15"},{"v":1.094834437086093,"d":"1.09"},{"v":1.0516239316239315,"d":"1.05"},{"v":1.1611513616702123,"d":"1.16"},"valor Cti"]
[null,"Energia mensual perdida por el campo captador",null,{"v":10849.194199880296,"d":"10,849"},{"v":9523.414979531794,"d":"9,523"},{"v":10754.410752736869,"d":"10,754"},{"v":10660.589861508277,"d":"10,661"},{"v":10895.708298941425,"d":"10,896"},{"v":10616.000874276824,"d":"10,616"},{"v":11298.537949301,"d":"11,299"},{"v":11002.339676977785,"d":"11,002"},{"v":10665.261088742047,"d":"10,665"},{"v":10803.118913074462,"d":"10,803"},{"v":10530.64481300519,"d":"10,531"},{"v":10798.291978266232,"d":"10,798"},{"v":128397.51338624221,"d":"128,398"},"KWh/mes"]
[null,"Relación entre energía perdida y demanda mensual",null,{"v":3.5974431673575045,"d":"3.60"},{"v":3.496172319417008,"d":"3.50"},{"v":3.7086548548544584,"d":"3.71"},{"v":3.9571292824565076,"d":"3.96"},{"v":4.084110070803686,"d":"4.08"},{"v":4.398784958518841,"d":"4.40"},{"v":4.870371164660143,"d":"4.87"},{"v":4.627015925898057,"d":"4.63"},{"v":4.419196137173515,"d":"4.42"},{"v":3.9632466459784697,"d":"3.96"},{"v":3.7525388889620075,"d":"3.75"},{"v":3.5805646927007553,"d":"3.58"},{"v":4.003187675938213,"d":"4.00"},"valor Xi"]
[null,"Porcentaje demanda aportado por sistema solar",null,{"v":0.4030036178734207,"d":"40.30%"},{"v":0.564064391276188,"d":"56.41%"},{"v":0.7338774980388323,"d":"73.39%"},{"v":0.8153523066065582,"d":"81.54%"},{"v":0.8681160406471582,"d":"86.81%"},{"v":0.9777936280434951,"d":"97.78%"},{"v":1.040559441857578,"d":"104.06%"},{"v":1.0151986134503999,"d":"101.52%"},{"v":0.9304987243104468,"d":"93.05%"},{"v":0.7051178385898653,"d":"70.51%"},{"v":0.49287638387983407,"d":"49.29%"},{"v":0.3401954157354316,"d":"34.02%"},{"v":0.7219928289834757,"d":"72.20%"},"Fracción F-chart"]
[]
[null,"(ESpro) Energía Solar Térmica Producida (kWh)",null,{"v":1215.3811221359001,"d":"1,215"},{"v":1536.4858429506387,"d":"1,536"},{"v":2128.108536648978,"d":"2,128"},{"v":2196.576334238783,"d":"2,197"},{"v":2315.9853638964455,"d":"2,316"},{"v":2359.8011969349127,"d":"2,360"},{"v":2413.943402843654,"d":"2,414"},{"v":2413.9877976776725,"d":"2,414"},{"v":2245.6599638185885,"d":"2,246"},{"v":1922.0282103173806,"d":"1,922"},{"v":1383.1451955432296,"d":"1,383"},{"v":1025.9637079781346,"d":"1,026"},{"v":23157.06667498432,"d":"23,157"},"kWh/mes"]
[null,"(PTdem) Perdidas Térmicas asociadas (kWh)",null,{"v":301.58069759999995,"d":"302"},{"v":272.39546880000006,"d":"272"},{"v":289.98144,"d":"290"},{"v":269.402112,"d":"269"},{"v":266.7829248,"d":"267"},{"v":241.339392,"d":"241"},{"v":231.98515199999997,"d":"232"},{"v":237.78478080000002,"d":"238"},{"v":241.339392,"d":"241"},{"v":272.5825535999999,"d":"273"},{"v":280.6272,"d":"281"},{"v":301.58069759999995,"d":"302"},{"v":3207.3818111999994,"d":"3,207"},"kWh/mes"]
[null,"(ESnet) Aporte Solar Neto (kWh) ",null,{"v":913.8004245359002,"d":"914"},{"v":1264.0903741506386,"d":"1,264"},{"v":1838.1270966489778,"d":"1,838"},{"v":1927.1742222387832,"d":"1,927"},{"v":2049.2024390964457,"d":"2,049"},{"v":2118.461804934913,"d":"2,118"},{"v":2181.9582508436542,"d":"2,182"},{"v":2176.2030168776723,"d":"2,176"},{"v":2004.3205718185884,"d":"2,004"},{"v":1649.4456567173806,"d":"1,649"},{"v":1102.5179955432295,"d":"1,103"},{"v":724.3830103781347,"d":"724"},{"v":19949.68486378432,"d":"19,950"},"kWh/mes"]
[]
[null,"ESTUDIO DE SOMBRAS SOBRE CARTA SOLAR CILINDRICA",{"$nulls":6},"CIRCUITO PRIMARIO"]
[]
[null,"% Obstrucción solar global en Invierno",null,{"v":0,"d":"0.00%"},{"$nulls":4},"DATOS DE SELECCIÓN DEL EQUIPO DE BOMBEO"]
[null,"% Obstruccion solar global en Verano",null,{"v":0,"d":"0.00%"}]
[{"$nulls":8},"Caudal",null,null,{"v":1.6463999999999999,"d":"1.65 m3/h"}]
[null,"% Obstruccion solar global Anual",null,{"v":0,"d":"0.00%"},{"$nulls":4},"Perdida de carga",null,null,{"v":1.3674923866122939,"d":"1.37 mca"}]
[]
[{"$nulls":8},"DATOS DE SELECCIÓN PARA EL INTERCAMBIADOR"]
[]
[{"$nulls":8},"Superficie min. de intercambio",null,null,{"v":4.9392,"d":"4.94 m²"},null,"(aplicable a serpentines)"]
[{"$nulls":8},"Potencia min.  Intercambiador",null,null,{"v":19.7568,"d":"19.76 kW"},null,"(aplicable a intercambiadores de placas)"]
[]
[{"$nulls":8},"DATOS DE SELECCIÓN DEL ",null,null,"DRAIN BACK"]
[]
[{"$nulls":8},"Volumen mínimo",null,null,{"v":127.12645005327221,"d":"127.13 litros"}]
[{"$nulls":8},"Presion valvula seguridad",null,null,{"v":10,"d":"10.00 bar"}]
[]
[{"$nulls":8},"Volumen en circuito (litros)",null,null,{"v":75.46277548893241,"d":"75.46 litros"}]
[{"$nulls":8},"Volumen dilatado (litros)",null,null,{"v":6.4143359165592555,"d":"6.41 litros"}]
[{"$nulls":8},"Volumen de reserva (litros)",null,null,{"v":3,"d":"3.00 litros"}]
[{"$nulls":8},"Volumen vaporizado (litros)",null,null,{"v":36.2208,"d":"36.22 litros"}]
[]
[{"$nulls":8},"15/13","18/16","22/20","28/26","35/33","42/40","54/52","Diámetro tubería"]
[{"$nulls":8},0,0,0,10,40,0,0,"ml de tuberia Cir. Primario"]
[]
[{"$nulls":3},"Ene","Feb","Mar","Abr","May","Jun","Jul","Ago","Sep","Oct","Nov","Dic","Anual"]
[null,"% Obstruccion sobre radiación DIRECTA",null,{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"}]
[null,"% Obstruccion sobre radiación GLOBAL",null,{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"},{"v":0,"d":"0.00%"}]

{"sheet":"C. Primario","index":8,"n_rows":30,"n_cols":53,"rows_kept":30,"merged":[[3,5,3,9],[3,11,3,15],[4,8,4,9],[4,14,4,15],[5,8,5,9],[5,14,5,15],[6,8,6,9],[6,14,6,15],[7,8,7,9],[7,14,7,15],[8,8,8,9],[9,8,9,9],[9,11,9,13],[9,14,9,15],[10,8,10,9],[12,5,12,9],[13,8,13,9],[14,8,14,9]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":1}
[{"$nulls":24},"15/13","18/16","22/20","28/26","35/33","42/40","54/52"]
[null,"CIRCUITO PRIMARIO SOLAR   (conexión captador con intercambiador o drainback)",{"$nulls":15},"Factor aumento por retorno",{"$nulls":3},{"v":2,"d":"2.00"},null,"Total",0,0,0,10,40,0,0]
[{"$nulls":26},"Volumen captador",2.352,"l/m2"]
[null,"Número total de captadores",14,14,null,"Datos selección bomba",{"$nulls":5},"Datos Vaso de expansión o Drain Back",{"$nulls":14},"Volumen total captadores",32.928,{"$nulls":22},"Primario","Wilo Yonos","General"]
[null,"Superficie de captación",{"v":32.928,"d":"32.93 m²"},null,null,"Perdida de carga lineal",null,null,{"v":0.8374923866122939,"d":"0.84 mca"},null,null,"Coeficiente exp. fluido",null,null,0.085,{"$nulls":11},"Serpentin 1",0,"num 1",1,{"$nulls":21},"Wilo Maxo","Gran caudal"]
[null,"Caudal por captador",{"v":50,"d":"50.00 l/h  m2"},null,null,"Perdida intercambiador",null,null,{"v":0.5,"d":"0.50 mca"},null,null,"Tarado valvula seguridad",null,null,{"v":10,"d":"10.00 bar"},{"$nulls":11},"Serpentin 2","0","num 1",0,{"$nulls":21},"Stratos"]
[null,"Caudal total",{"v":1646.3999999999999,"d":"1,646 l/h"},0.4573333333333333,null,"Perdida captadores",null,null,{"v":0.03,"d":"0.03 mca"},null,null,"Columna encima del vaso",null,null,{"v":15,"d":"15.00 m"},{"$nulls":11},"Serpentin ?¿?","NO",{"$nulls":22},"ACS","Stratos Z","Recirculacion"]
[null,"Fluido caloportador","agua glicolada",1.3,null,"Montaje de captadores",null,null,"paralelo",null,null,"Volumen interc. placas",null,null,{"v":4,"d":"4.00 litros"},{"$nulls":11},"Volumen intercambiador",4,null,"interior"]
[null,"Velocidad del fluido",{"v":1.5,"d":"1.50 m/s"},0,0,"Perdida carga adicional",null,null,{"v":0,"d":"0.00 mca"},{"$nulls":17},"Volumen en equipos (litros)",36.928,null,"exterior"]
[null,"Tipo de tubería","cobre",{"v":1,"d":"1.00"},null,"Caudal de la bomba",null,null,{"v":1.6463999999999999,"d":"1.65 m3/h"},null,null,"Volumen min del vaso",null,null,{"v":127.12645005327221,"d":"127.13 litros"},{"$nulls":11},"Presion absoluta final (Kg/cm2)",{"v":6.5,"d":"6.50"}]
[null,"Perdida de carga maxima (mmca /m)",38,null,null,"Perdida de carga TOTAL",null,null,{"v":1.3674923866122939,"d":"1.37 mca"},null,null,"Coeficiente de presión",null,null,{"v":1.8571428571428572,"d":"1.86"},null,null,"fluido 60º",null,3.85,"Ce KJ/kgK",{"$nulls":5},"Volumen util",{"v":45.63513591655925,"d":"45.64"}]
[0,"Caudal por acumulador ind.",{"v":102.89999999999999,"d":"102.90 l/h"},{"$nulls":8},"Volumen en circuito (litros)",null,null,{"v":75.46277548893241,"d":"75.46"},null,null,"fluido 60º",null,1010,"densidad Kg/m3",{"$nulls":5},"Presion absoluta inicial (Kg/cm2)",3]
[{"$nulls":5},"Perdidas termicas",{"$nulls":5},"Volumen dilatado (litros)",null,null,{"v":6.4143359165592555,"d":"6.41"},null,null,"caudal",null,{"v":1646.3999999999999,"d":"1,646 l/h"},{"$nulls":6},"coeficiente seguridad",1.5]
[{"$nulls":5},"Conductividad aislamiento",null,null,{"v":0.04,"d":"0.040 W/mK"},null,{"v":0.5179484112245625,"d":"Potencia 0.52 kW"},"Volumen de reserva (litros)",null,null,{"v":3,"d":"3.00"},null,null,"Potencia",null,{"v":106.70043999999999,"d":"106.70"},"kW"]
[{"$nulls":5},"Total perdida térmica",null,null,{"v":1134.307020581792,"d":"1134 kWh/año"},null,{"v":0.004854229384851296,"d":"0.49%"},"Volumen vaporizado (litros)",null,null,{"v":36.2208,"d":"36.22"},null,null,"4% potencia",null,{"v":4.268017599999999,"d":"4.27"},"kW",null,null,"http://www.wilo.es/instalador-hotwater/productos/?tx_wproducts_general%5Bproduct%5D=524&tx_wproducts_general%5Baction%5D=show&cHash=ad46cec350bed1d03e8485082a150ee5#.WdgF41u0OUk",{"$nulls":7},"http://productfinder.wilo.com/es/es/c0000003a0003b16700010023/product.html#tab=4",{"$nulls":6}," "]
[{"$nulls":5},"temperatura referencia",null,null,{"v":60,"d":"60.00"},{"$nulls":3}," ",{"$nulls":10},"( en rojo los diámetros que superan la velocidad o perdida de carga máxima)"]
[null,"Tramo","Núm. Captadores","Caudal ","Longitud ","Parte del ","Caudal ","Velocidad","Diámetro","Serie","Serie","Diámetro","Velocidad","Pérdida","+25%","Pérdida","Pérdida","Volumen",null,"Tipo de","Espesor","Perdida ",null,"D ext","15/13","18/16","22/20","28/26","35/33","42/40","54/52","35/33"]
[null,"Descripcion","a los que da ","adicional","del tramo","tramo mas","TOTAL","Máxima","Teórico Int","nominal","nominal","Nom. Int.","Cálculo","Tubería","Accesorios","Total","TOTAL","fluido",null,"Tramo","aislante","térmica",null,"D int",13,16,20,{"v":25.6,"d":"26"},{"v":32.6,"d":"33"},{"v":39.6,"d":"40"},{"v":51.6,"d":"52"},{"$nulls":4},0,0,0,0,15,0,0]
[null,null,"servicio el tramo","l/h","(m)","desfavorable","(l/s)","(m/s)","(mm)","CALCULO","SELEC.","(mm)","(m/s)","(mca /m)","(mca)","(mca)","(KPa)","(litros)",null,"(int / ext)","(mm)","(W)",null,"v (m/s)",{"v":3.445531864648211,"d":"3.45"},{"v":2.2745893950216707,"d":"2.27"},{"v":1.4557372128138693,"d":"1.46"},{"v":0.8885114824303401,"d":"0.89"},{"v":0.5479081684722305,"d":"0.55"},{"v":0.37132364371336324,"d":"0.37"},{"v":0.21869737588093702,"d":"0.22"},"22/20"]
[null,"TR1 IDA/RET 12 paneles distr. interior",14,0,{"v":15,"d":"15.00"},"SI",{"v":0.4573333333333333,"d":"0.46"},{"v":1.5,"d":"1.50"},{"v":19.702705146342176,"d":"19.70"},"35/33","35/33",{"v":32.6,"d":"32.60"},{"v":0.5479081684722305,"d":"0.55"},{"v":0.013570268082880248,"d":"0.014"},{"v":0.003392567020720062,"d":"0.003"},{"v":0.2544425265540047,"d":"0.25"},{"v":2.493536760229246,"d":"2.49"},{"v":12.520346281984084,"d":"12.52"},null,"interior",25,{"v":158.1302138722682,"d":"158"},null,"mca /m",{"v":1.0694022762414674,"d":"1.069"},{"v":0.3988431246752224,"d":"0.399"},{"v":0.1381909327552259,"d":"0.138"},{"v":0.04277915406664353,"d":"0.043"},{"v":0.013570268082880248,"d":"0.014"},{"v":0.005386664096229667,"d":"0.005"},{"v":0.0015320958806810925,"d":"0.002"},"35/33",14,{"v":0.2544425265540047,"d":"0.25"},{"v":12.520346281984084,"d":"12.52"}]
[]
[null,"Tramo","Núm. Captadores","Caudal ","Longitud ","Parte del ","Caudal ","Velocidad","Diámetro","Serie","Serie","Diámetro","Velocidad","Pérdida","+25%","Pérdida","Pérdida","Volumen",null,"Tipo de","Espesor","Perdida ",null,"D ext","15/13","18/16","22/20","28/26","35/33","42/40","54/52","35/33"]
[null,"Descripcion","a los que da ","adicional","del tramo","tramo mas","TOTAL","Máxima","Teórico Int","nominal","nominal","Nom. Int.","Cálculo","Tubería","Accesorios","Total","TOTAL","fluido",null,"Tramo","aislante","térmica",null,"D int",13,16,20,{"v":25.6,"d":"26"},{"v":32.6,"d":"33"},{"v":39.6,"d":"40"},{"v":51.6,"d":"52"},{"$nulls":4},0,0,0,0,5,0,0]
[null,null,"servicio el tramo","l/h","(m)","desfavorable","(l/s)","(m/s)","(mm)","CALCULO","SELEC.","(mm)","(m/s)","(mca /m)","(mca)","(mca)","(KPa)","(litros)",null,"(int / ext)","(mm)","(W)",null,"v (m/s)",{"v":3.445531864648211,"d":"3.45"},{"v":2.2745893950216707,"d":"2.27"},{"v":1.4557372128138693,"d":"1.46"},{"v":0.8885114824303401,"d":"0.89"},{"v":0.5479081684722305,"d":"0.55"},{"v":0.37132364371336324,"d":"0.37"},{"v":0.21869737588093702,"d":"0.22"},"22/20"]
[null,"TR1 IDA/RET grupo 1+2",14,0,{"v":5,"d":"5.00"},"SI",{"v":0.4573333333333333,"d":"0.46"},{"v":1.5,"d":"1.50"},{"v":19.702705146342176,"d":"19.70"},"35/33","35/33",{"v":32.6,"d":"32.60"},{"v":0.5479081684722305,"d":"0.55"},{"v":0.013570268082880248,"d":"0.014"},{"v":0.003392567020720062,"d":"0.003"},{"v":0.08481417551800155,"d":"0.08"},{"v":0.8311789200764153,"d":"0.83"},{"v":4.173448760661361,"d":"4.17"},null,"exterior",35,{"v":53.89446573614697,"d":"54"},null,"mca /m",{"v":1.0694022762414674,"d":"1.069"},{"v":0.3988431246752224,"d":"0.399"},{"v":0.1381909327552259,"d":"0.138"},{"v":0.04277915406664353,"d":"0.043"},{"v":0.013570268082880248,"d":"0.014"},{"v":0.005386664096229667,"d":"0.005"},{"v":0.0015320958806810925,"d":"0.002"},"35/33",14,{"v":0.08481417551800155,"d":"0.08"},{"v":4.173448760661361,"d":"4.17"}]
[]
[null,"Tramo","Núm. Captadores","Caudal ","Longitud ","Parte del ","Caudal ","Velocidad","Diámetro","Serie","Serie","Diámetro","Velocidad","Pérdida","+25%","Pérdida","Pérdida","Volumen",null,"Tipo de","Espesor","Perdida ",null,"D ext","15/13","18/16","22/20","28/26","35/33","42/40","54/52","28/26"]
[null,"Descripcion","a los que da ","adicional","del tramo","tramo mas","TOTAL","Máxima","Teórico Int","nominal","nominal","Nom. Int.","Cálculo","Tubería","Accesorios","Total","TOTAL","fluido",null,"Tramo","aislante","térmica",null,"D int",13,16,20,{"v":25.6,"d":"26"},{"v":32.6,"d":"33"},{"v":39.6,"d":"40"},{"v":51.6,"d":"52"},{"$nulls":4},0,0,0,5,0,0,0]
[null,null,"servicio el tramo","l/h","(m)","desfavorable","(l/s)","(m/s)","(mm)","CALCULO","SELEC.","(mm)","(m/s)","(mca /m)","(mca)","(mca)","(KPa)","(litros)",null,"(int / ext)","(mm)","(W)",null,"v (m/s)",{"v":1.7227659323241056,"d":"1.72"},{"v":1.1372946975108353,"d":"1.14"},{"v":0.7278686064069346,"d":"0.73"},{"v":0.44425574121517003,"d":"0.44"},{"v":0.2739540842361152,"d":"0.27"},{"v":0.18566182185668162,"d":"0.19"},{"v":0.10934868794046851,"d":"0.11"},"15/13"]
[null,"TR1 IDA/RET grupo 1+2",7,0,{"v":5,"d":"5.00"},"SI",{"v":0.22866666666666666,"d":"0.23"},{"v":1.5,"d":"1.50"},{"v":13.931916416697641,"d":"13.93"},"28/26","28/26",{"v":25.6,"d":"25.60"},{"v":0.44425574121517003,"d":"0.44"},{"v":0.012718318597462521,"d":"0.013"},{"v":0.0031795796493656304,"d":"0.003"},{"v":0.07948949123414076,"d":"0.08"},{"v":0.7789970140945794,"d":"0.78"},{"v":2.573592701820759,"d":"2.57"},null,"exterior",35,{"v":46.94952600386607,"d":"47"},null,"mca /m",{"v":0.3179351989266147,"d":"0.318"},{"v":0.118576770408423,"d":"0.119"},{"v":0.041084410115344326,"d":"0.041"},{"v":0.012718318597462521,"d":"0.013"},{"v":0.004034464839163882,"d":"0.004"},{"v":0.0016014648173415058,"d":"0.002"},{"v":0.0004554948305430789,"d":"0.000"},"28/26",7,{"v":0.07948949123414076,"d":"0.08"},{"v":2.573592701820759,"d":"2.57"}]

{"sheet":"C. Secundario","index":9,"n_rows":20,"n_cols":41,"rows_kept":20,"merged":[[1,22,1,26],[1,27,1,28],[3,5,3,9],[3,11,3,15],[4,8,4,9],[4,14,4,15],[5,8,5,9],[5,14,5,15],[6,8,6,9],[6,14,6,15],[7,14,7,15],[8,8,8,9],[9,8,9,9],[9,11,9,13],[9,14,9,15],[10,8,10,9],[12,5,12,9],[13,8,13,9],[14,8,14,9]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":1}
[{"$nulls":30},20,25,32,40,50,63,75]
[null,"CIRCUITO SECUNDARIO DISTRIBUIDO   (conexión acumulador central con intercambiadores individuales)",{"$nulls":20},"Factor aumento por retorno",{"$nulls":4},{"v":2,"d":"2.00"},null,null,0,0,0,3,0,0,0]
[{"$nulls":25},"Volumen captador",2.352,"l/m2"]
[null,"Número total de intercambiadores",1,25,null,"Datos selección bomba",{"$nulls":5},"Datos Vaso de expansión",{"$nulls":13},"Volumen total captadores",2.352]
[null,"Aplicar simultaneidad","NO",{"v":1,"d":"1.00"},null,"Perdida de carga lineal",null,null,{"v":0.10986156614051804,"d":"0.11 mca"},null,null,"Coeficiente exp. fluido",null,null,0.085,{"$nulls":10},"Serpentin 1",0,"num 1",1]
[null,"Caudal por intercambiador",{"v":1481.76,"d":"1482 l/h"},null,null,"Perdida Ud intercambiador",null,null,{"v":0.3,"d":"0.30 mca"},null,null,"Tarado valvula seguridad",null,null,{"v":10,"d":"10.00 bar"},{"$nulls":10},"Serpentin 2","0","num 1",0]
[null,"Caudal simultaneo total",{"v":1481.76,"d":"1,482 l/h"},0.4116,null,"Perdida TOTAL interc.",null,null,{"v":0.3,"d":"0.30 mca"},null,null,"Columna encima del vaso",null,null,{"v":15,"d":"15.00 m"},{"$nulls":10},"Serpentin ?¿?","NO"]
[null,"Fluido caloportador","agua",1,{"$nulls":7},"Volumen Ud interc. placas",null,null,{"v":1,"d":"1.00 litros"},{"$nulls":10},"Volumen intercambiador",1]
[null,"Velocidad del fluido",{"v":1.5,"d":"1.50 m/s"},0,null,"Perdida carga adicional",null,null,{"v":0,"d":"0.00 mca"},{"$nulls":16},"Volumen en equipos (litros)",3.352]
[null,"Tipo de tubería","PEX",{"v":1,"d":"1.00"},null,"Caudal de la bomba",null,null,{"v":1.48176,"d":"1.48 m3/h"},null,null,"Volumen min del vaso",null,null,{"v":37.67301821377713,"d":"37.67 litros"},{"$nulls":10},"Presion absoluta final (Kg/cm2)",{"v":6.5,"d":"6.50"}]
[null,"Perdida de carga maxima (mmca /m)",38,null,null,"Perdida de carga TOTAL",null,null,{"v":0.40986156614051805,"d":"0.41 mca"},null,null,"Coeficiente de presión",null,null,{"v":1.8571428571428572,"d":"1.86"},{"$nulls":10},"Volumen util",{"v":13.523647563919994,"d":"13.52"}]
[0,"Caudal por acumulador ind.",{"v":1481.76,"d":"1,481.76 l/h"},{"$nulls":8},"Volumen en circuito (litros)",null,null,{"v":93.36997134023521,"d":"93.37"},{"$nulls":10},"Presion absoluta inicial (Kg/cm2)",3]
[{"$nulls":5},"Perdidas termicas",{"$nulls":5},"Volumen dilatado (litros)",null,null,{"v":7.936447563919994,"d":"7.94"},{"$nulls":10},"coeficiente seguridad",1.5]
[{"$nulls":5},"Conductividad aislamiento",null,null,{"v":0.04,"d":"0.040 W/mK"},null,null,"Volumen de reserva (litros)",null,null,{"v":3,"d":"3.00"}]
[{"$nulls":5},"Total perdida térmica",null,null,{"v":80.72484420861012,"d":"81 kWh/año"},null,null,"Volumen vaporizado (litros)",null,null,{"v":2.5872,"d":"2.59"},{"$nulls":15},"http://productfinder.wilo.com/es/es/c0000003a0003b16700010023/product.html#tab=4"]
[{"$nulls":5},"temperatura referencia",null,null,{"v":45,"d":"45.00"},{"$nulls":13},"( en rojo los diámetros que superan la velocidad o perdida de carga máxima)"]
[null,"Tramo","Núm. Intercamb.","Caudal ","Longitud ","Parte del ","Caudal ","Velocidad","Diámetro","Serie","Serie","Diámetro","Velocidad","Pérdida","+25%","Pérdida","Pérdida","Volumen",null,"Espesor","Perdida ",null,"D ext",20,25,32,40,50,63,75,40]
[null,"Descripcion","a los que da ","adicional","del tramo","tramo mas","TOTAL","Máxima","Teórico Int","nominal","nominal","Nom. Int.","Cálculo","Tubería","Accesorios","Total","TOTAL","fluido",null,"aislante","térmica",null,"D int",14.6,18.2,23.4,29.2,36.5,{"v":46,"d":"46.0"},54.7,{"$nulls":4},0,0,0,3,0,0,0]
[null,null,"servicio el tramo","l/h","(m)","desfavorable","(l/s)","(m/s)","(mm)","CALCULO","SELEC.","(mm)","(m/s)","(mca /m)","(mca)","(mca)","(KPa)","(litros)",null,"(mm)","(W)",null,"v (m/s)",{"v":2.458554121847406,"d":"2.46"},{"v":1.5821319786649952,"d":"1.58"},{"v":0.9570921846245034,"d":"0.96"},{"v":0.6146385304618515,"d":"0.61"},{"v":0.39336865949558497,"d":"0.39"},{"v":0.2476679568114334,"d":"0.25"},{"v":0.17515027843848044,"d":"0.18"},25]
[null,"Intercambidor central",1,0,{"v":3,"d":"3.00"},"SI",{"v":0.4116,"d":"0.41"},{"v":1.5,"d":"1.50"},{"v":18.691627298748728,"d":"18.69"},40,40,{"v":29.2,"d":"29.20"},{"v":0.6146385304618515,"d":"0.61"},{"v":0.01464820881873574,"d":"0.015"},{"v":0.003662052204683935,"d":"0.004"},{"v":0.05493078307025902,"d":"0.05"},{"v":0.5383216740885384,"d":"0.54"},{"v":2.008985670117601,"d":"2.01"},null,25,{"v":18.43032972799318,"d":"18"},null,"mca /m",{"v":0.39416404113800607,"d":"0.394"},{"v":0.13836108974785008,"d":"0.138"},{"v":0.041935105904639454,"d":"0.042"},{"v":0.01464820881873574,"d":"0.015"},{"v":0.005075302831163895,"d":"0.005"},{"v":0.0016914274185246402,"d":"0.002"},{"v":0.0007428707638570066,"d":"0.001"},40,1,{"v":0.05493078307025902,"d":"0.05"},{"v":2.008985670117601,"d":"2.01"}]

{"sheet":"Acumuladores","index":10,"n_rows":55,"n_cols":25,"rows_kept":55,"merged":[[1,1,2,2],[3,14,3,19],[4,1,6,1],[4,2,6,2],[4,6,6,6],[4,7,6,7],[4,8,6,8],[4,10,6,10],[4,11,6,11],[4,12,6,12],[4,14,6,14],[4,15,6,15],[4,16,6,16],[4,17,6,17],[4,18,6,18],[4,19,6,19],[4,21,6,21],[4,23,6,23]],"flags":["formulas_cached_only"]}
[]
[null,"VOLVER A HOJA SOLAR"]
[]
[{"$nulls":14},"Datos conjuntos solares"]
[null,"FABRICANTE Y MODELO","Volumen de acumulación         (litros)",{"$nulls":3},"Capacidad Drain Back (litros)","Área intercambio serpentin (m2)","Volumen max en serpentin (litros)",null,"Altura deposito (mm)","Diámetro deposito (mm)","Peso en vacio",null,"Modulo solar asociado","Bombeo primario","Potencia max. bomba (W)","Altura máxima (metros)","Longitud máx. tuberia (metros)","Dim primario entrada /  salida",null,"Perdidas térmicas UA (W/K)",null,"Actualizado"]
[{"$nulls":4},"DRAIN BACK"]
[]
[null,"SD WE 75",75,null,"NO",null,"---",0.53,5,null,799,549,40,null,null,"---","---","---","---","---",{"$nulls":3},"2021-06-01"]
[null,"SD WE 100",100,null,"NO",null,"---",{"v":0.7,"d":"0.70"},7,null,947,697,50,null,null,"---","---","---","---","---",{"$nulls":3},"2021-06-01"]
[null,"SD WE 150",150,null,"NO",null,"---",0.85,8,null,1318,1068,69,null,null,"---","---","---","---","---",{"$nulls":3},"2021-06-01"]
[null,"SD Helioset 150 (FES 150)",150,null,"SI",null,8,{"v":1.3,"d":"1.30"},8,null,1064,600,69,null,"Saunier Duval  SRH 2.3 (cub. Incli./panel hor.)","2x GSHD 8",75,12,20,"DN 10/10",null,1.16,null,"2021-04-01"]
[null,"SD Helioset 250 (FES 250)",250,null,"SI",null,8,{"v":1.5,"d":"1.50"},9,null,1539,600,89,null,"Saunier Duval  SRD 2.3","2x GSHD 8",75,12,20,"DN 10/10",null,1.44,null,"2021-04-01"]
[null,"SD Helioset 350 (FES 350)",355,null,"SI",null,10,{"v":1.6,"d":"1.60"},10,null,1680,796,125,null,"Saunier Duval  SRD 2.3","2x GSHD 8",75,12,20,"DN 10/10",null,1.58,null,"2021-04-01"]
[null,"SD Interacumulador BDLE S/ 750S",750,null,"NO",null,"---",{"v":2.7,"d":"2.70"},16,null,1890,950,195,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Interacumulador BDLE S/ 1000S",{"v":1000,"d":"1,000"},null,"NO",null,"---",{"v":3.3,"d":"3.30"},20,null,2250,950,230,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Interacumulador BDLE S/ 1500S",{"v":1500,"d":"1,500"},null,"NO",null,"---",{"v":2.8,"d":"2.80"},17,null,1830,1360,415,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Interacumulador BDLE S/ 2000S",{"v":2000,"d":"2,000"},null,"NO",null,"---",{"v":3.4,"d":"3.40"},20,null,2280,1360,475,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Interacumulador BDLE S/ 2500S",{"v":2500,"d":"2,500"},null,"NO",null,"---",{"v":4.2,"d":"4.20"},25,null,2015,1660,690,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Acumulador BDLE 750",750,null,"NO",null,"---","---","---",null,1840,950,170,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Acumulador BDLE 1000",{"v":1000,"d":"1,000"},null,"NO",null,"---","---","---",null,2250,950,200,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Acumulador BDLE 1500",{"v":1500,"d":"1,500"},null,"NO",null,"---","---","---",null,1830,1360,390,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Acumulador BDLE 2000",{"v":2000,"d":"2,000"},null,"NO",null,"---","---","---",null,2280,1360,450,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Acumulador BDLE 2500",{"v":2500,"d":"2,500"},null,"NO",null,"---","---","---",null,2015,1660,630,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Acumulador BDLE 3000",{"v":3000,"d":"3,000"},null,"NO",null,"---","---","---",null,2305,1660,690,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Acumulador BDLE 3500",{"v":3500,"d":"3,500"},null,"NO",null,"---","---","---",null,2580,1660,755,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[null,"SD Acumulador BDLE 4000",{"v":4000,"d":"4,000"},null,"NO",null,"---","---","---",null,2310,1910,880,null,null,"---","---","---","---","---",{"$nulls":3},"2021-04-01"]
[]
[null,"Vaillant auroSTEP Plus 150 (VIH SN 150)",150,null,"SI",null,8,{"v":1.3,"d":"1.30"},"---",null,1082,605,110,null,"Vaillant  auroTHERM VFK 135 VD (vert)","2x GSHD 8",86,12,20,"DN 10/10",{"$nulls":3},"2021-04-01"]
[null,"Vaillant auroSTEP Plus 250  (VIH SN 250)",253,null,"SI",null,8,{"v":1.3,"d":"1.30"},"---",null,1692,605,130,null,"Vaillant  auroTHERM VFK 135 VD (vert)","2x GSHD 8",86,12,20,"DN 10/10",{"$nulls":3},"2021-04-01"]
[null,"Vaillant auroSTEP Plus 350 (VIH SN 350)",395,null,"SI",null,10,{"v":1.6,"d":"1.60"},"---",null,1592,814,140,null,"Vaillant  auroTHERM VFK 135 VD (vert)","2x GSHD 8",86,12,20,"DN 10/10",{"$nulls":3},"2021-04-01"]
[null,"Vaillant allSTORE VPS 300",303,null,"NO",null,"---","---","---",null,1735,780,70]
[null,"Vaillant allSTORE VPS 500",491,null,"NO",null,"---","---","---",null,1715,930,90]
[null,"Vaillant allSTORE VPS 800",778,null,"NO",null,"---","---","---",null,1846,1070,130]
[null,"Vaillant allSTORE VPS 1000",962,null,"NO",null,"---","---","---",null,2226,1070,145]
[null,"Vaillant allSTORE VPS 1500",{"v":1505,"d":"1,505"},null,"NO",null,"---","---","---",null,2205,1400,210]
[null,"Vaillant allSTORE VPS 2000",{"v":1917,"d":"1,917"},null,"NO",null,"---","---","---",null,2330,1500,240]
[]
[null,"ACV Drain Back 200",200,null,"SI",null,10,{"v":1.4,"d":"1.40"},9,null,1515,560,54,null,"ACS Helioplan 2,5 DB","Wilo-Yonos PICO-STG 15/13",85,12,20,"DN 10/10",{"$nulls":3},"2017-04-01","http://productfinder.wilo.com/com/es/Wilo/c0000002a0003a36300010023/c0000002a0003a4a200010023/c00000049000165be00020023/product.html"]
[null,"ACV Drain Back 300",300,null,"SI",null,11,{"v":1.6,"d":"1.60"},10,null,1755,640,68,null,"ACS Helioplan 2,5 DB","Wilo-Yonos PICO-STG 15/13",85,12,20,"DN 10/10",{"$nulls":3},"2017-04-01","http://productfinder.wilo.com/com/es/Wilo/c0000002a0003a36300010023/c0000002a0003a4a200010023/c00000049000165be00020023/product.html"]
[]
[null,"GrennHeiss  GH 200 DB",212,null,"SI",null,8.6,{"v":1.4,"d":"1.40"},9,null,1520,560,65,null,"GREENHEISS  GH Class 25V","Wilo STG 15-11",75,11,20,"DN 10/10",{"$nulls":3},"2017-04-01","http://productfinder.wilo.com/com/es/c0000000e0001b19500020023/_00000000000179d40001003a/product.html#tab=product_datasheet"]
[]
[null,"Lapesa Interacumulador MVV 1500 SB",{"v":1500,"d":"1,500"},null,"NO",null,"---",{"v":2.8,"d":"2.80"},17,null,1830,1360,430,null,null,"---","---","---","---","---",{"$nulls":3},"2017-04-01"]
[null,"Lapesa Interacumulador MVV 2000 SB",{"v":2000,"d":"2,000"},null,"NO",null,"---",{"v":3.4,"d":"3.40"},19,null,2280,1360,495,null,null,"---","---","---","---","---",{"$nulls":3},"2017-04-01"]
[null,"Lapesa Interacumulador MVV 2500 SB",{"v":2500,"d":"2,500"},null,"NO",null,"---",{"v":4.8,"d":"4.80"},28,null,2015,1660,675,null,null,"---","---","---","---","---",{"$nulls":3},"2017-04-01"]
[null,"Lapesa Interacumulador MVV 3000 SB",{"v":3000,"d":"3,000"},null,"NO",null,"---",{"v":5,"d":"5.00"},29,null,2305,1660,740,null,null,"---","---","---","---","---",{"$nulls":3},"2017-04-01"]
[]
[null,"Lapesa acumulador MVV 1500 RB",{"v":1500,"d":"1,500"},null,"NO",null,"---","---","---",null,1830,1360,400,null,null,"---","---","---","---","---",{"$nulls":3},"2021-05-01"]
[null,"Lapesa acumulador MVV 2000 RB",{"v":2000,"d":"2,000"},null,"NO",null,"---","---","---",null,2280,1360,460,null,null,"---","---","---","---","---",{"$nulls":3},"2021-05-01"]
[null,"Lapesa acumulador MVV 2500 RB",{"v":2500,"d":"2,500"},null,"NO",null,"---","---","---",null,2015,1660,635,null,null,"---","---","---","---","---",{"$nulls":3},"2021-05-01"]
[null,"Lapesa acumulador MVV 3000 RB",{"v":3000,"d":"3,000"},null,"NO",null,"---","---","---",null,2305,1660,705,null,null,"---","---","---","---","---",{"$nulls":3},"2021-05-01"]
[null,"Lapesa acumulador MVV 3500 RB",{"v":3500,"d":"3,500"},null,"NO",null,"---","---","---",null,2580,1660,755,null,null,"---","---","---","---","---"]
[null,"Lapesa acumulador MVV 4000 RB",{"v":4000,"d":"4,000"},null,"NO",null,"---","---","---",null,2310,1910,915,null,null,"---","---","---","---","---"]
[]
[null,"TERMICOL Termidrain DB 200",212,null,"SI",null,8.6,{"v":1.4,"d":"1.40"},9,null,1530,625,120,null,"TERMICOL T20MS","Wilo-Yonos PICO-STG 15/13",85,12,20,"DN 10/10",{"$nulls":3},"2021-01-01"]

{"sheet":"Captadores ANT","index":11,"n_rows":59,"n_cols":15,"rows_kept":59,"hidden":true,"merged":[[1,1,2,12],[4,1,6,1],[4,2,6,2],[4,3,6,3],[4,14,6,14]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":2}
[]
[null,"VOLVER A HOJA SOLAR"]
[]
[]
[null,"FABRICANTE Y MODELO","Superficie apertura (m2)","Superficie absorvedor (m2)","Longitud","Factor de eficacia","Coeficiente lineal","Coeficiente cuadratico","Coeficiente global","Volumen contenido","Caudal","Caudal","K50 ",null,"Actualizado"]
[{"$nulls":4},"en maxima","(Rendimiento)","de perdidas (a1)","de perdidas (a2)","de perdidas",null,"ensayo","funcionamiento","Factor angulo"]
[{"$nulls":4},"pendiente",null,"(W/m²K)","(W/m²K)","(W/m²K)","litros","l / h m2","l / h m2","incidencia"]
[1,"Fagor Solaria-2.4 G AL",{"v":2.17,"d":"2.170"},null,{"v":1.8083333333333333,"d":"1.808"},{"v":0.693,"d":"0.6930"},{"v":4.39,"d":"4.3900"},{"v":0.018,"d":"0.0180"},{"v":5.109999999999999,"d":"5.1100"},{"v":1.3,"d":"1.3000"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.92,"d":"0.9200"},null,"2015-03-01"]
[1,"Fagor Solaria-2.8 G AL",{"v":2.58,"d":"2.580"},null,{"v":2.1500000000000004,"d":"2.150"},{"v":0.693,"d":"0.6930"},{"v":4.39,"d":"4.3900"},{"v":0.018,"d":"0.0180"},{"v":5.109999999999999,"d":"5.1100"},{"v":1.5,"d":"1.5000"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.92,"d":"0.9200"},null,"2015-03-01"]
[1,"Fagor Solaria-2.4 AL AL",{"v":2.17,"d":"2.170"},null,{"v":1.8083333333333333,"d":"1.808"},{"v":0.722,"d":"0.7220"},{"v":3.39,"d":"3.3900"},{"v":0.014,"d":"0.0140"},{"v":3.95,"d":"3.9500"},{"v":1.3,"d":"1.3000"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.92,"d":"0.9200"},null,"2015-03-01"]
[1,"Fagor Solaria-2.8 AL AL",{"v":2.58,"d":"2.580"},null,{"v":2.1500000000000004,"d":"2.150"},{"v":0.722,"d":"0.7220"},{"v":3.39,"d":"3.3900"},{"v":0.014,"d":"0.0140"},{"v":3.95,"d":"3.9500"},{"v":1.5,"d":"1.5000"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.92,"d":"0.9200"},null,"2015-03-01"]
[1,"Saunier Duval  SCV 2.3 (cub. Incli./panel vert)",2.352,2.327,2.035,{"v":0.792,"d":"0.7920"},{"v":2.804,"d":"2.8040"},{"v":0.055,"d":"0.0550"},{"v":5.004,"d":"5.0040"},{"v":1.85,"d":"1.8500"},48.87,{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Saunier Duval  SRH 2.3 (cub. Incli./panel hor.)",{"v":2.35,"d":"2.350"},2.327,1.232,{"v":0.81,"d":"0.8100"},{"v":3.32,"d":"3.3200"},{"v":0.023,"d":"0.0230"},{"v":4.24,"d":"4.2400"},{"v":2.16,"d":"2.1600"},53.57,{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Saunier Duval  SRV 2.3 (cub. Plana/panel vert)",{"v":2.35,"d":"2.350"},2.327,2.035,{"v":0.79,"d":"0.7900"},2.4141,{"v":0.049,"d":"0.0490"},4.3741,{"v":1.85,"d":"1.8500"},48.97,{"v":50,"d":"50.00"},{"v":0.95,"d":"0.9500"},null,"2017-04-01"]
[1,"Saunier Duval  SRD 2.3",2.327,2.327,2.035,{"v":0.801,"d":"0.8010"},{"v":3.761,"d":"3.7610"},{"v":0.012,"d":"0.0120"},{"v":4.241,"d":"4.2410"},{"v":1.85,"d":"1.8500"},52.04,{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Vaillant  auroTHERM VFK 125 (vert)",2.352,2.327,2.033,{"v":0.753,"d":"0.7530"},{"v":3.936,"d":"3.9360"},{"v":0.017,"d":"0.0170"},{"v":4.616,"d":"4.6160"},{"v":1.85,"d":"1.8500"},{"v":45,"d":"45.00"},{"v":45,"d":"45.00"},{"v":0.89,"d":"0.8900"},null,"2017-04-01"]
[1,"Vaillant  auroTHERM VFK 135 VD (vert)",2.352,2.327,2.033,{"v":0.814,"d":"0.8140"},{"v":3.761,"d":"3.7610"},{"v":0.012,"d":"0.0120"},{"v":4.241,"d":"4.2410"},{"v":1.46,"d":"1.4600"},{"v":45,"d":"45.00"},{"v":45,"d":"45.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Vaillant  auroTHERM VFK 135 HD (hor.)",2.352,2.327,1.233,{"v":0.801,"d":"0.8010"},{"v":3.761,"d":"3.7610"},{"v":0.012,"d":"0.0120"},{"v":4.241,"d":"4.2410"},{"v":1.35,"d":"1.3500"},{"v":45,"d":"45.00"},{"v":45,"d":"45.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[null,"Vaillant  auroTHERM VFK 145 H (hor.)",2.352,2.327,1.233,{"v":0.801,"d":"0.8010"},{"v":3.32,"d":"3.3200"},{"v":0.023,"d":"0.0230"},{"v":4.24,"d":"4.2400"},{"v":2.16,"d":"2.1600"},{"v":45,"d":"45.00"},{"v":45,"d":"45.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Vaillant  auroTHERM VFK 145 V (vert)",2.352,2.327,2.033,{"v":0.79,"d":"0.7900"},{"v":2.414,"d":"2.4140"},{"v":0.049,"d":"0.0490"},{"v":4.3740000000000006,"d":"4.3740"},{"v":1.85,"d":"1.8500"},{"v":45,"d":"45.00"},{"v":45,"d":"45.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Viessman Vitosol 100-F SVA (vert)",2.324,null,{"v":2.38,"d":"2.380"},{"v":0.76,"d":"0.7600"},{"v":4.13,"d":"4.1300"},0.0182,{"v":4.858,"d":"4.8580"},{"v":1.48,"d":"1.4800"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Viessman Vitosol 100-F SVB (vert)",2.324,null,{"v":2.38,"d":"2.380"},{"v":0.754,"d":"0.7540"},4.0108,0.0114,4.4668,{"v":1.67,"d":"1.6700"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Viessman Vitosol 100-F SHA (hor)",2.324,null,1.056,{"v":0.76,"d":"0.7600"},{"v":4.13,"d":"4.1300"},0.0114,{"v":4.586,"d":"4.5860"},{"v":2.33,"d":"2.3300"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Viessman Vitosol 100-F SHB (hor)",2.324,null,1.056,{"v":0.754,"d":"0.7540"},4.0108,0.0114,4.4668,{"v":2.33,"d":"2.3300"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Viessman Vitosol 200-F SV2A (vert)",2.324,null,{"v":2.38,"d":"2.380"},{"v":0.792,"d":"0.7920"},{"v":4.04,"d":"4.0400"},0.0182,{"v":4.768,"d":"4.7680"},{"v":1.83,"d":"1.8300"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"Viessman Vitosol 200-F SH2A (hor)",2.324,null,1.056,{"v":0.792,"d":"0.7920"},{"v":4.04,"d":"4.0400"},0.0182,{"v":4.768,"d":"4.7680"},{"v":2.48,"d":"2.4800"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"ACS Helioplan 2,5 DB",2.404,null,{"v":2.15,"d":"2.150"},{"v":0.788,"d":"0.7880"},{"v":3.26,"d":"3.2600"},{"v":0.015,"d":"0.0150"},{"v":3.86,"d":"3.8600"},{"v":1.7,"d":"1.7000"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"GREENHEISS  GH Class 25V",{"v":2.32,"d":"2.320"},null,{"v":2.15,"d":"2.150"},{"v":0.77,"d":"0.7700"},{"v":3.911,"d":"3.9110"},{"v":0.01,"d":"0.0100"},{"v":4.311,"d":"4.3110"},{"v":1.34,"d":"1.3400"},{"v":50,"d":"50.00"},{"v":50,"d":"50.00"},{"v":0.91,"d":"0.9100"},null,"2017-04-01"]
[1,"TERMICOL T20MS",{"v":1.87,"d":"1.870"},null,{"v":2.13,"d":"2.130"},{"v":0.812,"d":"0.8120"},{"v":3.812,"d":"3.8120"},{"v":0.021,"d":"0.0210"},{"v":4.652,"d":"4.6520"},{"v":1.29,"d":"1.2900"},{"v":40,"d":"40.00"},{"v":40,"d":"40.00"},{"v":0.91,"d":"0.9100"},null,"2019-01-01"]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[0,{"$nulls":7},{"v":0,"d":"0.0000"}]
[21,"COLECTOR PROMEDIO",2.437,null,{"v":1.9312698412698415,"d":"1.931"},{"v":0.8078095238095238,"d":"0.808"},{"v":3.8283666666666676,"d":"3.828"},{"v":0.021466666666666672,"d":"0.021"},{"v":4.687033333333335,"d":"4.6870"},{"v":1.83,"d":"1.830"},{"v":50.87857142857143,"d":"50.88"},null,{"v":0.9561904761904763,"d":"0.956"}]

{"sheet":"Disipadores","index":12,"n_rows":34,"n_cols":18,"rows_kept":34,"hidden":true,"flags":["formulas_cached_only"]}
[]
[{"$nulls":4},"Sin disipador"]
[null,"Disipadores de calor dinámicos",null,null,"Disipador dinámico",{"$nulls":7},"https://www.youtube.com/watch?v=vQLtdR8R_bM"]
[{"$nulls":4},"Sistema Drain-Back"]
[null,"Salvador Scoda"]
[{"$nulls":16},"Wilo Stratos STG"]
[null,"Modelo","m2 colector","Potencia Kw","Caudal l/h","Tª salida","m.c.a",{"$nulls":9},"Wilo Star-STG"]
[null,"BD 08",10,8,600,76.76,0.13,{"$nulls":9},"Wilo Top-STG"]
[null,"BD 16",20,16,1200,77.19,0.27]
[null,"BD 24",30,24,1800,77.33,0.74,{"$nulls":9},"rendimiento ",{"v":0.25,"d":"25%"}]
[null,"BD 32",40,32,2400,77.38,0.72]
[null,"BD 40",50,40,3000,77.6,1.19,{"$nulls":9},"parelelo"]
[null,"BD 48",60,48,3600,77.7,1.83]
[null,"BD 56",70,56,4200,77.47,0.95]
[null,"BD 64",80,64,4800,77.54,1.45]
[null,"BD 72",90,72,5400,77.18,1.37]
[null,"BD 80",100,80,6000,76.96,1.23]
[null,"BD 96",120,96,7200,78.19,1.32]
[null,"BD 112",140,112,8400,77.79,0.72]
[null,"BD 120",150,120,9000,76.86,0.87]
[null,"BD 144",180,144,10800,78,1.04]
[null,"BD 160",200,160,12000,77.44,1.17]
[null,"BD 184",230,184,13800,77.96,1.41]
[null,"BD 200",250,200,15000,77.23,1.54]
[null,"BD 224",280,224,16800,77.55,1.79]
[null,"BD 240",300,240,18000,77.11,1.92]
[null,"BD 264",330,264,19800,77.29,2.13]
[]
[]
[null,"m2 paneles",32.928]
[null,"Modelo","BD 32"]
[null,"Potencia",32,{"$nulls":13},"valvula de 3 vias en serie"]
[null,"Caudal",2400]
[null,"mca",0.72]

{"sheet":"Fabricantes","index":13,"n_rows":112,"n_cols":2,"rows_kept":112,"hidden":true,"flags":["formulas_cached_only"]}
["FA_Codigo","FA_Nombre"]
[212,"Abora Energy S.L."]
[152,"ACV España"]
[165,"ADISA"]
[180,"Adisa."]
[72,"Alwec"]
[114,"Amordad"]
[81,"Andater"]
[65,"Ariston"]
[3,"Astersa Aplicaciones Solares"]
[119,"Aterrasolar"]
[103,"Atlantic-Thermor"]
[102,"Atlantic-Ygnis"]
[217,"BAETULENN"]
[4,"Baxi Calefaccion"]
[67,"Bionergy del Principado"]
[49,"Buderus"]
[77,"Chaffoteaux"]
[50,"CHROMAGEN ESPAÑA, S.L.U"]
[91,"Cidersol"]
[73,"Cliber Grupo Clima"]
[108,"Cointra"]
[194,"Comercial Saclima S. L."]
[68,"Constante Solar"]
[94,"Cosmosolar"]
[82,"Daikin"]
[122,"Del Paso Solar, S.L."]
[79,"Diseño y Proyectos Energéticos"]
[70,"Distribuidora de Aparatos de Calefacción"]
[182,"Domusa Calefacción S. Coop."]
[105,"DPE"]
[174,"ECOMESH"]
[196,"Energía Solar Santa Fe"]
[64,"Energie Solaire Hispano"]
[184,"ENERPAL PROYECTOS ENERGÉTICOS, S.L.U."]
[66,"Enerplasol"]
[116,"Eurofred"]
[46,"Fagor"]
[151,"Fercofloor"]
[107,"Ferroli"]
[80,"Frigicoll"]
[124,"Fujisol"]
[11,"Gamesa Solar"]
[99,"GE XXI ENERGIAS"]
[197,"GREENHEISS"]
[101,"Groupe Atlantic"]
[87,"Heatsun"]
[115,"Heleos Hispania"]
[199,"Helioakmi, Distribuidor Oficial García e Hijos"]
[98,"Hucu Solar España"]
[191,"IAXXON ENERGÍA"]
[74,"Icma Sistemas"]
[63,"Immosolar"]
[15,"IMS CALEFACCIÓN SL"]
[83,"Ingesol Canarias, S.L.N.E."]
[166,"INGESOL CANARIAS, S.L.N.E.."]
[164,"JOSEDINAR PLACAS SOLARES S.L"]
[17,"Junkers"]
[109,"Lamborghini"]
[88,"Lapesa"]
[84,"LKN Sistemes"]
[185,"LUMELCO"]
[177,"Magen Eco Energy"]
[92,"Match Energies"]
[112,"Nagaterm"]
[153,"NOVASOL"]
[69,"Nueva Terrain"]
[19,"OCV"]
[190,"Openplus"]
[162,"ORKLI"]
[47,"Paradigma"]
[206,"PLEION SRL"]
[186,"POWER PANEL"]
[179,"PROMASOL"]
[71,"Reno Energy"]
[169,"Robert Bosch S.L.U"]
[23,"Roth"]
[76,"Saltoki"]
[155,"Salvador Escoda"]
[24,"Saunier Duval"]
[26,"Schuco"]
[175,"SEDICAL"]
[104,"Sime Hispania"]
[29,"Solahart Industries"]
[148,"SOLARFOCUS GmbH"]
[55,"SOLARIS"]
[172,"Solartecnik"]
[110,"Solcrafte Iberica"]
[121,"Soleco"]
[54,"Soliker"]
[159,"SOLIMPEKS SOLAR"]
[120,"Solvis Iberica"]
[53,"Sonnenkraft"]
[154,"Soterna"]
[188,"SUICALSA, S.A."]
[195,"Sunaitec"]
[90,"Tea-08"]
[210,"TECNA"]
[62,"Termicol"]
[158,"TERMOCLUB, S.A."]
[118,"Thernoslate"]
[85,"TIFELL"]
[39,"TiSUN"]
[187,"TiSUN"]
[123,"Trisolar"]
[138,"TUSOL Sistemas Energéticos, S.L."]
[57,"Vaillant"]
[183,"Vaillant"]
[42,"Viessmann"]
[43,"Wagner Solar"]
[173,"Wagner Solar."]
[45,"Wolf"]

{"sheet":"Paneles","index":14,"n_rows":665,"n_cols":13,"rows_kept":665,"hidden":true,"flags":["formulas_cached_only"]}
["CA_Codigo","CA_Modelo","CA_Fabricante","CA_Area","CA_n0","CA_a1","CA_a2","CA_Cabal","CA_k50","CA_Laboratorio","CA_Ensayo","CA_Fecha","CA_Homologacion"]
[768,"2.3 Cu",121,2.1,0.767,5.34,0.043,50,0.093,13,"EL 003-09",42140,"GPS-8075"]
[769,"2.3 CuS",121,2.07,0.784,4.02,0.0302,50,0.93,13,"EL006-04",42141,"GPS-8069"]
[25,"5000 S",11,2.099,0.764,4.4,0.017,72,0.94,7,"22/LECS-DER/2008",42373,"NPS 15311"]
[24,"5000 ST",11,2.1,0.728,3.4,0.007,72,0.93,7,"24/101.104/2004",42373,"NPS 15211"]
[191,"A-21",29,2.15,0.789,2.9,0.006,72,0.92,6,"CA/RPT/4451/005/INTA/10",41165,"NPS-25810"]
[980,"ACV GREENSUN 2.2 HDB",152,1.99,0.82,3.734,0.018,72,0.94,3,"30.1699.0-4-1",43870,"NPS-8418"]
[976,"ACV GREENSUN 2.2 HS",152,1.99,0.788,3.911,0.01,59.69,0.96,3,"30.2367.0",43870,"NPS-7818"]
[979,"ACV GREENSUN 2.2 VDB",152,1.99,0.82,3.734,0.018,72,0.94,3,"30.1699.0-4-1",43870,"NPS-8218"]
[975,"ACV GREENSUN 2.2 VS",152,1.99,0.788,3.911,0.01,59.4,0.96,3,"30.1699.0-1-1",43870,"NPS-7718"]
[982,"ACV GREENSUN 2.6 HDB",152,2.32,0.81,3.683,0.017,72,0.93,3,"30,1699",43870,"NPS-8318"]
[978,"ACV GREENSUN 2.6 HS",152,2.32,0.77,3.442,0.016,59.4,0.96,3,"30.2367.0",43870,"NPS-8018"]
[981,"ACV GREENSUN 2.6 VDB",152,2.32,0.81,3.683,0.017,72,0.93,3,"30,1699",43870,"NPS-8118"]
[977,"ACV GREENSUN 2.6 VS",152,2.32,0.77,3.442,0.016,59.4,0.96,3,"30.2367.0-6-1",43870,"NPS-7918"]
[845,"ACV HEAT - PIPE 15",152,1.395,0.734,1.529,0.0166,70.5,1.26,16,"KTB NR. 2007-07-en",42223,"NPS-25313"]
[846,"ACV HEAT - PIPE 20",152,1.86,0.734,1.529,0.0166,70.5,1.26,16,"KTB NR. 2007-07-en",42223,"NPS-25413"]
[701,"ACV Kaplan 2.0",152,1.79,0.793,3.3,0.043,74.0111,0.88,6,"CA/RPT/4451/006/INTA/09",42109,"NPS 25811"]
[839,"ACV Kaplan 2.2 H",152,2.04,0.75,3.98,0.03,72,0.98,6,"CA/rpt/4451/009/INTA/12",42155,"NPS-26813"]
[703,"ACV Kaplan 2.4",152,2.39,0.772,4,0.029,73.5062,0.88,6,"CA/RPT/4451/019/INTA/08",41620,"NPS 53811"]
[702,"ACV Kaplan 3.0",152,2.58,0.78,3,0.053,75.3488,0.88,6,"CA/RPT/4451/008/INTA/09",41554,"NPS 41211"]
[704,"ACV Kaplan 3.3 V",152,2.85,0.841,3.95,0.02,72,0.88,6,"CA/RPT/4451/013/INTA/11",41665,"NPS 23712"]
[700,"ACV Kaplan S 2.1 H",152,1.88,0.802,3.82,0.0095,71.8,0.93,2,"C1280LPEN",42478,"GPS-8487"]
[699,"ACV Kaplan S 2.6 V",152,2.26,0.817,3.75,0.0112,70.8,0.93,2,"C1284LPEN",41789,"GPS-8483"]
[843,"ACV U Pipe 15",152,1.35,0.65,1.585,0.002,49,1.4973,5,"07COL536/1",42193,"NPS-26213"]
[844,"ACV U Pipe 20",152,1.8,0.65,1.585,0.002,49,1.4973,5,"07COL536/1",42193,"NPS-26313"]
[955,"ACV U Pipe 30",152,2.67,0.65,1.585,0.002,49,1.4973,5,"07COL536/1",43224,"GPS-8514"]
[917,"ADISOL BLUE 2.00A",180,1.88,0.786,3.536,0.016,68.4,0.88,3,"30.0771.0",44141,"GPS-8605"]
[918,"ADISOL BLUE 2.90A",180,2.73,0.778,3.339,0.014,68.4,0.88,3,"30.0771.1-2",44141,"GPS-8605"]
[913,"ADISOL HN-2.2",180,1.99,0.82,3.734,0.018,72,0.94,11,"30,1699",44162,"GPS-8633"]
[915,"ADISOL HN-2.6",180,2.32,0.81,3.683,0.017,57.6,0.93,11,"30,1699",44162,"GPS-8633"]
[912,"ADISOL VN-2.2",180,1.99,0.788,3.911,0.01,72,0.94,11,"30,1699",44162,"GPS-8633"]
[914,"ADISOL VN-2.6",180,2.32,0.77,3.442,0.016,72,0.95,11,"30,1699",44162,"GPS-8633"]
[988,"aH60SK",212,1.64,0.66,5.7,0,70.24,0.93,12,"Test Report 05/2019",44462,"NPS-9219"]
[989,"aH72SK",212,1.96,0.7,5.98,0,1.92,0.95,12,"Test Report 06/2019",44462,"NPS-9319"]
[589,"ALTER-TE-2360",90,2.18,0.773,3.743,0.021,72,0.93,3,"30.1074.0-1-1",41950,"NPS-47611"]
[496,"ALW-1.8V",72,1.767,0.748,3.718,0.0141,46.8,0.92,3,"30.109.0-2-1",41416,"NPS-0910"]
[498,"ALW-2.4V1",72,2.35,0.749,3.708,0.0136,60,0.91,4,"KTB-2008-47",41416,"NPS-1110"]
[495,"ALW-2.6H",72,2.497,0.759,4.241,0.033,70,0.94,4,"KTB-2009-16",41390,"NPS-0810"]
[499,"ALW-2.6V",72,2.514,0.749,3.708,0.0136,46.8,0.95,3,"30.1096.0-3-1",41416,"NPS-1210"]
[497,"ALW-2V1",72,1.96,0.749,3.708,0.0136,60,0.91,4,"KTB-2008-47",41416,"NPS-1010"]
[737,"Am- Tubosol 3000-15T",114,1.206,0.734,1.529,0.0166,30,0.95,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-19812"]
[738,"Am- Tubosol 3000-20T",114,1.607,0.734,1.529,0.0166,30,0.95,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-20112"]
[675,"Amordad Solar Am-Tubosol 3000-10 R",114,0.808,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-19512"]
[676,"Amordad Solar Am-Tubosol 3000-12 R",114,0.964,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-19612"]
[677,"Amordad Solar Am-Tubosol 3000-14 R",114,1.125,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-19712"]
[678,"Amordad Solar Am-Tubosol 3000-15 R",114,1.206,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-19812"]
[679,"Amordad Solar Am-Tubosol 3000-16 R",114,1.286,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-19912"]
[680,"Amordad Solar Am-Tubosol 3000-18 R",114,1.447,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-20012"]
[681,"Amordad Solar Am-Tubosol 3000-20 R",114,1.607,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-20112"]
[682,"Amordad Solar Am-Tubosol 3000-24 R",114,1.929,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-20212"]
[683,"Amordad Solar Am-Tubosol 3000-25 R",114,2.009,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-20312"]
[684,"Amordad Solar Am-Tubosol 3000-28 R",114,2.25,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-20412"]
[685,"Amordad Solar Am-Tubosol 3000-30 R",114,2.411,0.734,1.529,0.0166,72,0.92,4,"KTB Nr. 2007-07-k1-en",41747,"NPS-20512"]
[561,"AP-10",80,0.94,0.687,1.505,0.011,61,1.26,5,"09COL805",42030,"GPS-8280"]
[562,"AP-20",80,1.88,0.687,1.505,0.011,61,1.26,5,"09COL805",42030,"GPS-8280"]
[563,"AP-30",80,2.82,0.687,1.505,0.011,61,1.26,5,"09COL805",42030,"GPS-8280"]
[181,"AR20",4,2.153,0.773,1.43,0.0059,75,0.92,8,"82-08/D",41690,"GPS-8208"]
[182,"AR30",4,3.228,0.779,1.07,0.0135,75,0.92,8,"83-08/D",41690,"GPS-8208"]
[4,"AS-1.8 M",3,1.767,0.748,3.718,0.0141,46.8,0.92,3,"30.109.0-2-1",41599,"NPS-49711"]
[6,"AS-2.0 M",3,2,0.776,3.635,0.013,57.6,0.94,3,"30.0273.0",41077,"NPS-0208"]
[5,"AS-2.4 M",3,2.37,0.773,3.809,0.011,50.4,0.95,3,"30.027.1",41237,"NPS-317010"]
[3,"AS-2.6 M",3,2.514,0.749,3.708,0.0136,46.8,0.95,3,"30.1096.0-3-1",41403,"NPS-22011"]
[271,"AS-2.6 MH",3,2.497,0.759,4.241,0.0033,70,0.94,4,"KTB-2009-16",41545,"NPS-39211"]
[552,"ASL-1.5",79,1.38,0.734,3.622,0.016,72,0.85,5,"10COL972",41558,"NPS-41811"]
[553,"ASL-1.8",79,1.72,0.725,3.509,0.015,72,0.85,5,"10COL973",41558,"NPS-41911"]
[657,"ASL-2.0",105,1.86,0.725,3.509,0.015,72,0.85,5,"10COL973",41558,"NPS-42011"]
[554,"ASL-2.0",79,1.86,0.725,3.509,0.015,72,0.85,5,"10COL973",41558,"NPS-42011"]
[555,"ASL-2.0H",79,1.86,0.725,3.509,0.015,72,0.85,5,"10COL973",41558,"NPS-42111"]
[658,"ASL-2.0H",105,1.86,0.725,3.509,0.015,72,0.85,5,"10COL973",41558,"NPS-42111"]
[659,"ASL-2.3",105,2.23,0.725,3.509,0.015,72,0.85,5,"10COL973",41558,"NPS-42211"]
[556,"ASL-2.3",79,2.23,0.725,3.509,0.015,72,0.85,5,"10COL973",41558,"NPS-42211"]
[557,"ASL-2.7",79,2.57,0.725,3.509,0.015,72,0.85,5,"10COL973",41558,"NPS-42311"]
[660,"ASL-2.7",105,2.57,0.725,3.509,0.015,72,0.85,5,"10COL973",41558,"NPS - 41811"]
[748,"ATERRASOLAR  E 1.8",119,1.79,0.746,4.57,0.012,68.4,0.94,3,"30.1401.0-3-1",41942,"NPS-20013"]
[744,"ATERRASOLAR  N 2.0",119,1.99,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",42050,"NPS-21513"]
[749,"ATERRASOLAR E 2.0",119,1.99,0.746,4.57,0.012,68.4,0.94,3,"30.1401.0-3-1",41942,"NPS-20113"]
[743,"ATERRASOLAR N 1.8",119,1.79,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",42050,"NPS-20013"]
[745,"ATERRASOLAR N 2.4",119,2.44,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",42050,"NPS-21613"]
[746,"ATERRASOLAR N 2.6",119,2.53,0.769,3.957,0.01,72,0.94,3,"30.1520.0-3-1",42050,"NPS-21713"]
[747,"ATERRASOLAR N 2.6H",119,2.53,0.769,3.957,0.01,72,0.94,3,"30.1520.0-3-1",42050,"NPS-21813"]
[741,"ATERRASOLAR T 2.0",119,2.03,0.792,3.722,0.018,176.4,0.94,3,"30.1520.0-4-1",42050,"NPS-22113"]
[742,"ATERRASOLAR T 2.4",119,2.32,0.797,3.756,0.016,176.4,0.94,3,"30.1520.0-6-1",42050,"NPS-22213"]
[635,"Atlantic CSP 2.0V",102,1.9,0.758,3.895,0.02,40,0.89,3,"30.1143.0-1-2",41790,"NPS-23412"]
[638,"Atlantic CSP 2.0V",103,1.9,0.758,3.895,0.02,40,0.89,3,"30.1143.0-1-2",42155,"NPS-23412"]
[706,"Atlantic CSP 2.0V-1",102,1.86,0.748,4.036,0.016,40,0.9,3,"30.1835.0-6-1",42069,"GPS-8513"]
[709,"Atlantic CSP 2.0V-1",103,1.86,0.748,4.036,0.016,40,0.9,3,"30.1225.0-1-1",42155,"GPS-8513"]
[636,"Atlantic CSP 2.5H",102,2.4,0.758,3.895,0.02,40,0.89,3,"30.1225.0-1-1",41790,"NPS-23612"]
[639,"Atlantic CSP 2.5H",103,2.4,0.758,3.895,0.02,40,0.89,3,"30.1225.0-1-1",42155,"NPS-23612"]
[707,"Atlantic CSP 2.5H-1",102,2.26,0.748,4.036,0.016,40,0.9,3,"30.1835.0-6-1",42069,"GPS-8513"]
[710,"Atlantic CSP 2.5H-1",103,2.26,0.748,4.036,0.016,40,0.9,3,"30.1225.0-1-1",42155,"GPS-8513"]
[634,"Atlantic CSP 2.5V",102,2.4,0.769,3.946,0.017,40,0.85,3,"30.1225.0-1-1",41790,"NPS-23512"]
[637,"Atlantic CSP 2.5V",103,2.4,0.769,3.946,0.017,40,0.85,3,"30.1225.0-1-1",42155,"NPS-23512"]
[708,"Atlantic CSP 2.5V-1",103,2.26,0.753,3.813,0.019,40,0.86,3,"30.1225.0-1-1",42155,"GPS-8513"]
[705,"Atlantic CSP 2.5V-1",102,2.26,0.753,3.813,0.019,40,0.86,3,"30.1835.0-6-1",42069,"GPS-8513"]
[999,"BAESOL B10 i2,5 O",217,2.33,0.772,3.762,0.014,48,0.96,11,"078/000219",44760,"GPS-8626"]
[1000,"BAESOL B10 i2,5 V",217,2.33,0.689,3.862,0.013,48,0.96,11,"30.2367.0-6-1",44030,"GPS-8627"]
[998,"BAESOL B20 T10",217,1.6,0.636,0.654,0.013,88,1.23,15,"04COL349/2",44602,"GPS-8624"]
[997,"BAESOL B20 T14",217,2.23,0.588,0.605,0.007,30,1.23,15,"14COL1193",44602,"GPS-8622"]
[1002,"BAESOL B20 T15",217,2.68,0.615,0.85,0.009,20,1.05,21,"RP.2018.COL.202.1b",44602,"GPS-8651"]
[1001,"BAESOL B20 T21",217,4.02,0.609,0.69,0.005,20,1.14,21,"RP.2018.COL.202.1",44602,"GPS-8650"]
[500,"Basic ALW 1.8",72,1.77,0.746,4.57,0.012,68.4,0.94,3,"30.1401.0-3-1",41225,"NPS-14211"]
[501,"Basic ALW 2.0",72,1.96,0.756,4.887,0.009,68.4,0.94,3,"30.1401.0-3-1",41225,"NPS-14311"]
[833,"C10PLUS",138,9.26,0.804,3.201,0.015,72,0.8,9,"21219755_EN_P_GK3502 MPR",42273,"NPS-37913"]
[831,"C2.0SOL",138,1.92,0.717,3.556,0.014,72,0.97,4,"2012-09",42273,"NPS-37613"]
[830,"C2.5SOL",138,2.148,0.724,3.348,0.0165,72,0.97,4,"2012-09",42273,"NPS-37713"]
[761,"C253I",120,2.388,0.798,3.43,0.016,62,0.94,8,"145-08/KD",42209,"GPS-8355"]
[753,"C253I",120,2.388,0.798,3.43,0.016,62,0.94,8,"145-08/KD",42209,"GPS-8355"]
[754,"C253S",120,2.388,0.798,3.43,0.016,62,0.94,8,"145-08/KD",42209,"GPS-8405"]
[762,"C253S",120,2.388,0.798,3.43,0.016,62,0.94,8,"145-08/KD",42209,"GPS-8355"]
[832,"C5PLUS",138,4.64,0.801,3.188,0.015,72,0.8,9,"21219755_EN_P_GK3502 MPR",42273,"NPS-37813"]
[439,"Captador AS",64,1.832,0.954,8.91,0.047,80.8,0.99,2,"C421",41587,"GPS-8317"]
[983,"Chromagen RM 12-01",50,1.85,0.406,0.949,0.011,70,1.35,27,"161107081GZU-001",44325,"NPS-2819"]
[591,"CIDSOL_HT",91,1.95,0.816,3.497,0.018,160,0.95,3,"30.1493.0",41393,"NPS-21011"]
[253,"CKE 1.0 S",49,1.95,0.689,4.174,0.017,72,0.96,3,"30.1216.0-1-2",42050,"NPS-11010"]
[255,"CKN 1.0 S",49,1.94,0.756,4.052,0.0138,72,0.95,4,"2009-26",42050,"NPS-11210"]
[696,"CKN2,0",17,2.091,0.761,4.083,0.012,68.4,0.94,9,"21218975_ EN2_Bosch",42036,"NPS-1013"]
[558,"CO 2010 SV",80,2,0.747,3.791,0.022,75,0.96,3,"30.1151.0-1-1",42317,"GPS-8427"]
[560,"CO 2500 SH horizontal",80,2.5,0.747,3.35,0.02,75,0.96,3,"30.1151.0-2-2",42317,"GPS-8422"]
[559,"CO 2570 S",80,2.65,0.704,3.555,0.01,76,0.96,5,"07COL625/1",42317,"GPS-8093"]
[796,"COINTRA Icaro VRFA 2.0",107,1.89,0.76,3.656,0.016,72,0.87,9,"21221972_R_VMFA, 21221972 P VMFA",42418,"NPS-7214"]
[797,"COINTRA Icaro VRFA 2.3",107,2.226,0.76,3.656,0.016,72,0.87,9,"21221972_R_VMFA, 21221972 P VMFA",42418,"NPS-7314"]
[799,"COINTRA Icaro VRFA 2.8",107,2.69,0.768,3.591,0.016,72,0.87,9,"21221972_R_VMFA, 21221972 P VMFA",42418,"NPS-7414"]
[735,"CONSTANTE SOLAR CU-0210-P",68,0.42,0.784,5.09,0.023,72,0.94,3,"30.0892.2",42125,"NPS-15413"]
[733,"CONSTANTE SOLAR CU-1208-P",68,2.44,0.791,3.644,0.016,72,0.94,3,"30.0731.1-1",42125,"NPS-15213"]
[734,"CONSTANTE SOLAR NT-1010-P",68,2.03,0.801,3.738,0.017,72,0.94,3,"30.0738.0-2",42125,"NPS-15313"]
[223,"CPC 14 STAR AZZURRO INOX",47,2.33,0.644,0.749,0.0005,61.2,0.98,5,"06COL456",42109,"NPS-33011"]
[224,"CPC 21 STAR AZZURRO INOX",47,3.47,0.644,0.749,0.0005,61.2,0.98,5,"06COL456",42109,"NPS-33111"]
[225,"CPC 30 STAR AZZURRO INOX",47,3,0.644,0.749,0.0005,61.2,0.98,5,"06COL456",42109,"NPS-33211"]
[227,"CPC 32 ALLSSTAR INOX",47,3.21,0.644,0.749,0.0005,61.2,0.98,5,"06COL456",42109,"NPS-33411"]
[228,"CPC 40 ALLSSTAR INOX",47,4.01,0.644,0.749,0.0005,61.2,0.98,5,"06COL456",42109,"NPS-33511"]
[226,"CPC 45 STAR AZZURRO INOX",47,4.5,0.644,0.749,0.0005,61.2,0.98,5,"06COL456",42109,"NPS-33311"]
[825,"CPC ML 2890",15,2.89,0.823,3.86,0,72,0.88,6,"CA/RPT/4451/013/INTA/11-1",42524,"NPS 2314"]
[863,"CPC-S1",148,2.523,0.727,3.948,0.022,183.1,0.93,14,"2.04.00360.1.0-1",42175,"NPS-24313"]
[471,"CSA-18",68,1.767,0.748,3.718,0.0141,46.8,0.92,3,"30.1096.0-2-1",42125,"NPS-12411"]
[470,"CSA-26H",68,2.497,0.759,4.241,0.0033,70,0.094,4,"KTB-2009-16",42125,"NPS-12311"]
[472,"CSE-18",68,1.77,0.746,4.57,0.012,68.4,0.94,3,"30.1401.0-3-1",42125,"NPS-12811"]
[473,"CSE-20",68,1.96,0.756,4.887,0.009,68.4,0.94,3,"30.1401.0-3-1",42125,"NPS-12911"]
[476,"CSN-18",68,1.77,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",42125,"NPS-13211"]
[477,"CSN-20",68,1.96,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42125,"NPS-13311"]
[478,"CSN-24",68,2.41,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42125,"NPS-13411"]
[479,"CSN-26",68,2.49,0.769,3.957,0.01,72,0.94,3,"30.1520.0-3-1",42125,"NPS-13511"]
[437,"CSO 21",47,1.33,0.745,2.007,0.0005,62,0.98,5,"06 COL",42109,"NPS-32911"]
[474,"CST-20",68,2,0.792,3.722,0.018,176.4,0.94,3,"30.1520.0-4-1",42125,"NPS-13011"]
[475,"CST-24",68,2.3,0.797,3.756,0.016,176.4,0.94,3,"30.1520.0-6-1",42125,"NPS-13111"]
[361,"CTE 117CU4",26,2.34,0.744,3.383,0.015,78,0.92,15,"08CO702/1",42043,"NPS-4610"]
[66,"CTE 215 CH",26,1.88,0.82,4.068,0.012,72,0.94,15,"10COL870",42043,"NPS-32910"]
[67,"CTE 220 CH 2",26,2.49,0.792,3.818,0.017,57.6,0.96,11,"30.1093.0-5-1",41561,"NPS-42711"]
[187,"CTE 220 CH 5",26,2.507,0.806,3.9,0.0129,72,0.94,10,"98-10KD/64-10KQ",42043,"NPS-33010"]
[188,"CTE 319 CH",26,2.34,0.797,4.403,0.009,72,0.91,15,"10COL868/1",42043,"NPS-33810"]
[71,"CTE 520 CH",26,2.5,0.796,4.021,0.011,57.6,0.96,11,"30.1093.0-1-2",42057,"NPS-42411"]
[77,"CTE 520 CH 1",26,2.5,0.771,3.589,0.014,57.6,0.96,11,"30.1093.0-2-1",41561,"NPS-42611"]
[69,"CTE 520 CH 2",26,2.5,0.779,3.718,0.018,57.6,0.95,11,"30.1093.0-4-2",41561,"NPS-42511"]
[189,"CTE 520 CH1",26,2.52,0.771,3.589,0.013,57.6,0.96,11,"30.1093.0-2-1",41334,"NPS-17509"]
[438,"Cubierta Solar AS",64,1.832,0.954,9,0.01,80.8,0.99,2,"C420",41587,"GPS-8317"]
[440,"CuSel 26",64,2.364,0.751,3.389,0.013,72,0.96,17,"2.04.00555.1.0-1a-LT",41453,"GPS-8373"]
[441,"CuSel 30",64,2.57,0.765,3.944,0.009,64.3,0.96,17,"2.04.00480.1.0-7",41453,"GPS-8372"]
[834,"CV2.5PLUS",138,1.66,0.605,0.85,0.01,88,0.921,5,"04COL349_2",42299,"NPS-41213"]
[727,"DPE/ASL 1,5",105,1.38,0.734,3.622,0.016,72,0.85,5,"10COL972",41558,"NPS-41811"]
[728,"DPE/ASL 1,8",105,1.7,0.725,3.509,0.015,72,0.85,5,"10COL974",41558,"NPS 41911"]
[721,"DPE/DRS 1,5",105,1.32,0.8,4.19,0.021,81.85,0.87,20,"4055D1",41705,"NPS-14712"]
[722,"DPE/DRS 1,8",105,1.62,0.8,4.82,0.003,82.53,0.87,20,"4057D1",41705,"NPS-14812"]
[723,"DPE/DRS 2,0",105,1.78,0.8,4.82,0.003,82.53,0.87,20,"4057D1",41705,"NPS-14912"]
[724,"DPE/DRS 2,3",105,2.05,0.8,4.82,0.003,82.53,0.87,20,"4057D1",41705,"NPS-15012"]
[725,"DPE/DRSH 2,0",105,1.78,0.8,4.82,0.003,82.53,0.87,20,"4057D1",41705,"NPS-8510"]
[726,"DPE/DRSH 2,3",105,2.05,0.8,4.82,0.003,82.53,0.87,20,"4057D1",41705,"NPS-8610"]
[880,"DPS ECO1700",122,1.64,0.736,3.636,0.02,115.2,0.95,11,"30.2367.1",42722,"NPS-30014"]
[881,"DPS ECO2000",122,1.88,0.736,3.636,0.02,115.2,0.95,11,"30.2367.0-1-1",42722,"NPS-30814"]
[882,"DPS ECO2100",122,2,0.736,3.636,0.02,115.2,0.95,11,"30.2367.0-2-1",42722,"NPS-30914"]
[883,"DPS ECO2200",122,2.08,0.736,3.636,0.02,115.2,0.95,11,"30.2367.0-3-1",42722,"NPS-31014"]
[886,"DPS ECO2400",122,2.33,0.736,3.636,0.02,115.2,0.95,11,"30.2367.1",43803,"NPS-31114"]
[887,"DPS ECO2500",122,2.39,0.736,3.636,0.02,115.2,0.95,11,"30.2367.1",42722,"NPS-31214"]
[879,"DPS HSH2200",122,2,0.698,3.401,0.013,59.45,0.96,11,"30.2367.0",44245,"NPS-319"]
[878,"DPS HSH2600",122,2.33,0.707,3.43,0.016,59.45,0.96,11,"30.2367.0-4-1",44245,"NPS-29914"]
[888,"DPS HSM2200",122,1.99,0.82,3.734,0.018,72,0.94,11,"30.1699.0",43870,"NPS-5114"]
[889,"DPS HSM2600",122,2.32,0.81,3.683,0.017,72,0.93,11,"30.1699.0",43870,"NPS-3418"]
[884,"DPS VSH2200",122,1.99,0.788,3.911,0.01,59.45,0.96,11,"30.2367.0",44245,"NPS-4514"]
[885,"DPS VSH2600",122,2.32,0.77,3.442,0.016,59.45,0.96,11,"30.2367.0",44245,"NPS-4614"]
[890,"DPS VSM2200",122,1.99,0.82,3.734,0.018,72,0.94,11,"30.1699.0",43870,"NPS-4914"]
[891,"DPS VSM2600",122,2.32,0.81,3.683,0.017,72,0.93,11,"30.1699.0",43870,"NPS-4814"]
[546,"DRS-1.5",79,1.37,0.77,4.03,0.02,81.82,0.87,20,"4055D1",41012,"NPS-7110"]
[547,"DRS-1.8",79,1.7,0.74,4.45,0.002,82.54,0.87,20,"4057DE1",41012,"NPS-7210"]
[656,"DRS-2.0",105,1.81,0.8,4.82,0.003,82.54,0.87,20,"4057DE1",41756,"NPS-14912"]
[550,"DRS-2.0",79,1.87,0.74,4.45,0.002,82.54,0.87,20,"4057DE1",41012,"NPS-7310"]
[548,"DRS-2.0H",79,1.87,0.74,4.45,0.002,82.54,0.87,20,"4057DE1",41012,"NPS-8510"]
[654,"DRS-2.0H",105,1.81,0.8,4.82,0.003,82.54,0.87,20,"4057DE1",41756,"NPS-21512"]
[551,"DRS-2.3",79,2.22,0.74,4.45,0.002,82.54,0.87,20,"4057DE1",41012,"NPS-7410"]
[549,"DRS-2.3H",79,2.22,0.74,4.45,0.002,82.54,0.87,20,"4057DE1",41012,"NPS-8610"]
[655,"DRS-2.3H",105,2.05,0.8,4.82,0.003,82.54,0.87,20,"4057DE1",41756,"NPS-21612"]
[920,"DS DRAIN 2.11",182,1.89,0.81,4.335,0.006,72,0.958,5,"12COL1113OEM01",43036,"NPS-24515"]
[921,"DS DRAIN 2.51",182,2.23,0.816,4.096,0.01,72,0.957,5,"12COL1114OEM01",43036,"NPS-24615"]
[965,"ECO 1700",153,1.72,0.699,3.454,0.019,70,0.96,3,"30.2367..0-1-1, 30.2367.0-2-1, 30.2367.0-3-1, 30.2",43503,"NPS-11218"]
[303,"ECO 18",3,1.77,0.746,4.57,0.012,68.4,0.94,3,"30.1401.0-3-1",41942,"NPS-29010"]
[305,"ECO 20",3,2.01,0.756,4.887,0.009,72,0.93,3,"30.1401.0-1-1",41942,"NPS-29210"]
[966,"ECO 2000",153,1.96,0.699,3.454,0.019,70,0.96,3,"30.2367..0-1-1, 30.2367.0-2-1, 30.2367.0-3-1, 30.2",43503,"NPS-10818"]
[304,"ECO 20M",3,1.96,0.756,4.887,0.009,68.4,0.94,3,"30.1401.0-3-1",41942,"NPS-29110"]
[967,"ECO 2100",153,2.09,0.699,3.454,0.019,70,0.96,3,"30.2367..0-1-1, 30.2367.0-2-1, 30.2367.0-3-1, 30.2",43503,"NPS-11018"]
[968,"ECO 2200",153,2.17,0.699,3.454,0.019,70,0.96,3,"30.2367..0-1-1, 30.2367.0-2-1, 30.2367.0-3-1, 30.2",43503,"NPS-11218"]
[969,"ECO 2400",153,2.4,0.699,3.454,0.019,70,0.96,3,"30.2367..0-1-1, 30.2367.0-2-1, 30.2367.0-3-1, 30.2",43503,"NPS-10918"]
[970,"ECO 2500",153,2.48,0.75,3.54,0.015,60,0.96,3,"30.2367..0-1-1, 30.2367.0-2-1, 30.2367.0-3-1, 30.2",43503,"NPS-11118"]
[911,"ECOMESH V230/00",174,1.64,0.507,4.934,0.021,72,0.94,3,"30.2614.0-2-1",43177,"NPS-12216"]
[910,"ECOMESH-THERM",174,1.727,0.738,3.6,0.017,69.54,0.777,20,"4154DE4",43270,"NPS-9116"]
[943,"Ecotop VHM 2.1",107,1.82,0.808,3.334,0.02,144,0.95,3,"30.2047.0",43454,"NPS-29116"]
[946,"Ecotop VHM 2.7",107,2.36,0.815,3.368,0.019,144,0.93,3,"30.2047.0",43442,"NPS-29216"]
[995,"Ecotop VHM 2.7 N",107,2.62,0.776,3.02,0.019,82.8,0.95,3,"30.3139.1",44340,"NPS-3819"]
[571,"EKSV 26P",82,2.364,0.784,4.25,0.0072,85.04,0.94,2,"C1149QPEN",41953,"NP-28310"]
[922,"ENERPAL / ST-1",184,2.213,0.77,3.231,0.014,67.86,0.96,3,"30.0166.0",43986,"NPS-9718"]
[590,"ENER-TE-2000",90,1.853,0.726,6.73,0.0211,71.497,0.84,19,"EL007-09",41784,"NPS-9510"]
[514,"Enertres CES 2504",74,2.49,0.769,3.957,0.01,72,0.94,3,"30.1520.0-3-1",41329,"NPS-29111"]
[210,"ENERTRES CS 2004",43,2.009,0.78,3.95,0.0139,72,0.88,8,"142-10/KD",41258,"NPS 12011"]
[211,"ENERTRES CS 2402",43,2.369,0.844,3.48,0.0154,72,0.95,8,"14-08/D",41872,"NPS 12111"]
[513,"Enertres CS 2504-H",74,2.497,0.759,4.241,0.0033,46.8,0.95,3,"30.1096.0-3-1",41390,"NPS-29011"]
[603,"EPI 12",94,1.613,0.765,3.4151,0.022,72.5,0.887,26,"KT08-03I",41603,"NPS-51911"]
[605,"EPI 16",94,1.955,0.721,5.8355,0.0264,72.5,0.887,26,"KT08-03I",41603,"NPS-52111"]
[604,"EPI 20",94,1.303,0.776,4.0079,0.016,71.3,0.855,26,"KT08-04I, II",41603,"NPS-52011"]
[602,"EPI 25",94,1.768,0.765,3.4151,0.022,72.5,0.887,26,"KT08-03I",41603,"NPS-51811"]
[601,"EPI 54",94,2.26,0.765,3.4151,0.022,72.5,0.887,26,"KT08-03I",41603,"NPS-51711"]
[873,"ESCOSOL AKU 12",155,1.206,0.734,1.1,0.017,90,0.94,7,"10.v1/DER-LECS/2009",42800,"GPS-8343"]
[874,"ESCOSOL AKU 16",155,1.6,0.734,1.1,0.017,90,0.94,7,"10.v1/DER-LECS/2009",42800,"GPS-8343"]
[875,"ESCOSOL AKU 20",155,2.03,0.734,1.1,0.017,90,0.94,7,"14/DER-LECS/2008",42807,"GPS-8247"]
[633,"ESCOSOL CPC ML 3.0 TINOX",155,2.67,0.754,2.9,0.052,75,0.96,6,"CA/RPT/4451/008",42109,"NPS-3611"]
[872,"ESCOSOL CPC ML 3.0 TINOX PLUS",155,2.67,0.823,3.86,0,72,0.88,6,"CA/RPT/4451/013/INTA/11-i",42399,"NPS-8414"]
[957,"ESCOSOL FMAX 2.0",155,1.86,0.83,3.93,0.015,82.65,0.96,20,"4195DE2",43510,"GPS-8608"]
[956,"ESCOSOL FMAX 2.4",155,2.23,0.83,3.93,0.015,82.65,0.96,20,"4195DE2",43510,"GPS-8608"]
[958,"ESCOSOL FMAX 2.8",155,2.57,0.823,3.36,0.013,82.65,0.96,20,"4195DE2",43510,"GPS-8608"]
[900,"ESCOSOL STAR ECO V15 SELECTIVO W 2.0",155,1.78,0.764,4.78,0.0003,72,0.777,20,"4154 DE3",43127,"GPS-8594"]
[901,"ESCOSOL STAR ECO V15 SELECTIVO W 2.5",155,2.52,0.764,4.78,0.0003,72,0.777,20,"4154 DE3",43127,"GPS-8594"]
[240,"ESCOSOL SUNMAX H 24",155,2.27,0.547,1.134,0.023,162,1.68,9,"21211536",41067,"GPS-8408"]
[238,"ESCOSOL SUNMAX HP 15",155,1.42,0.547,1.134,0.023,162,1.68,9,"21211536",41067,"GPS-8408"]
[239,"ESCOSOL SUNMAX HP 20",155,1.89,0.547,1.134,0.023,162,1.68,9,"21211536",41067,"GPS-8408"]
[241,"ESCOSOL SUNMAX HP 26",155,2.46,0.547,1.134,0.023,162,1.68,9,"21211536",41067,"GPS-8408"]
[242,"ESCOSOL SUNMAX HP 30",155,2.83,0.547,1.134,0.023,162,1.68,9,"21211536",41067,"GPS-8408"]
[237,"ESCOSOL SUNMAX HP 6",155,0.567,0.488,2.222,0.008,162,1.68,9,"21211536",41067,"GPS-8408"]
[442,"ESDF-10",64,1.074,0.781,1.44,0.0062,72,0.92,8,"19-09/KD",41172,"GPS-8416"]
[443,"ESDF-20",64,2.153,0.779,1.07,0.0135,72,0.92,8,"106-06/D3",41172,"GPS-8416"]
[444,"ESDF-30",64,3.228,0.779,1.07,0.0135,72,0.92,8,"107-06/D3",41172,"GPS-8416"]
[445,"ESDF-V",64,1.054,0.783,1.061,0.023,65.2,0.96,9,"2121216_R",41301,"GPS-8433"]
[446,"ESHP95-10",64,1.074,0.726,1.55,0.0058,72,0.91,8,"35-09/KD",41244,"GPS-8430"]
[447,"ESHP95-20",64,2.157,0.738,1.17,0.0082,72,0.92,8,"109-06/D3",41244,"GPS-8430"]
[448,"ESHP95-30",64,3.229,0.727,0.85,0.0093,72,0.92,8,"110-06/D3",41244,"GPS-8430"]
[197,"Euro L20 AR",43,2.369,0.844,3.48,0.0154,72,0.95,8,"14-08/D",41992,"NPS -4311"]
[198,"Euro L20 MQ AR",43,2.369,0.842,3.62,0.016,72,0.94,8,"119-09/KD",41992,"NPS-31810"]
[199,"Euro L42 HTF",43,2.009,0.78,3.95,0.0139,72,0.88,8,"142-10/KD",41992,"NPS-33110"]
[755,"F552I",120,5.16,0.823,3.586,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[763,"F552I",120,5.16,0.823,3.586,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[756,"F552S",120,5.16,0.823,3.586,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[764,"F552S",120,5.16,0.823,3.586,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[765,"F652I",120,6.45,0.823,3.586,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[757,"F652I",120,6.45,0.823,3.586,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[766,"F652S",120,6.45,0.823,3.586,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[758,"F652S",120,6.45,0.823,3.586,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[759,"F802I",120,7.74,0.823,3.856,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[767,"F802S",120,7.74,0.823,3.586,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[760,"F802S",120,7.74,0.823,3.586,0.015,72,0.922,24,"KTB Nr. 2003-08",42209,"GPS-8217"]
[330,"Fachada IFK",53,2.28,0.738,3.578,0.14,133.2,0.92,5,"07COL595/1",41911,"NPS-25610"]
[815,"FC 2.0",151,1.86,0.718,5.084,0.0135,72,0.85,24,"2009-20-k4-b",42525,"NPS-21014"]
[817,"FC 2.2M",151,1.99,0.788,3.911,0.01,72,0.94,3,"30.1699-1-1 Anexo 6",42488,"NPS-16314"]
[820,"FC 2.5M",151,2.32,0.788,3.911,0.01,72,0.95,3,"30.1699-0-3-1",42485,"NPS-16214"]
[519,"FC 2.6 S",151,2.514,0.759,4.241,0.0033,46.8,0.95,3,"30.1096.0-3-1",41416,"NPS-10810"]
[515,"FC 2.6 SH",151,2.497,0.759,4.241,0.0033,70,0.94,4,"KTB-2009-16",41416,"NPS-10410"]
[252,"FCB 1 S",17,1.95,0.689,4.174,0.017,72,0.96,3,"30.1216.0-1-2",42050,"NPS-10910"]
[695,"FCB-2S",17,2.091,0.71,3.681,0.013,68.4,0.94,9,"21220433_ EN_Bosch",42036,"NPS-0913"]
[254,"FCC 1 S",17,1.94,0.756,4.052,0.0138,72,0.95,4,"2009-26",42050,"NPS-11110"]
[694,"FCC-2S",17,2.091,0.761,4.083,0.012,68.4,0.94,9,"21218975_ EN2_Bosch",42036,"NPS-0813"]
[663,"FERROLI Ecotop HF 2.3",107,2.21,0.737,3.775,0.018,126,0.89,9,"21211249a_HF2.3",42057,"NPS-3811"]
[661,"FERROLI Ecotop VF 2.0",107,1.87,0.755,3.72,0.017,126,0.89,9,"21211664a_VF2.0",42057,"NPS-3611"]
[662,"FERROLI Ecotop VF 2.3",107,2.21,0.75,3.706,0.009,126,0.89,9,"21210486a",42057,"NPS-3711"]
[664,"FERROLI Ecotop VF 2.8",107,2.657,0.771,3.24,0.026,126,0.89,9,"21211664a_VF2.8",42057,"NPS-3911"]
[791,"FERROLI Ecotop VRFA 2.0",107,1.89,0.76,3.656,0.016,72,0.87,9,"21221972_R_VMFA, 21221972 P VMFA",42418,"NPS-6914"]
[792,"FERROLI Ecotop VRFA 2.3",107,2.226,0.76,3.656,0.016,72,0.87,9,"21221972_R_VMFA, 21221972 P VMFA",42418,"NPS-7014"]
[793,"FERROLI Ecotop VRFA 2.8",107,2.69,0.768,3.591,0.016,72,0.87,9,"21221972_R_VMFA, 21221972 P VMFA",42418,"NPS-7114"]
[650,"FKC-2 S",17,2.25,0.766,3.216,0.015,82.8,0.92,9,"21216476_EN_Bosch",42109,"NPS-55111"]
[651,"FKC-2 W",17,2.25,0.77,3.871,0.012,82.8,0.92,9,"21218052_EN_Bosch",42109,"NPS-54911"]
[37,"FKT-1 S",17,2.24,0.811,3.653,0.0146,72,0.937,4,"2006-29-3N",42043,"NPS-48911"]
[246,"FKT-1 W",17,2.24,0.811,3.653,0.0146,72,0.937,4,"2006-29-en",42050,"NPS-49011"]
[195,"FM-S 2.55 MODULKOLLEKTOR",39,2.364,0.781,3.65,0.0155,68.4,0.9,8,"138-10/KD",41588,"NPS-28610"]
[193,"FM-W 2.0 MODULKOLLEKTOR",39,1.847,0.79,3.76,0.015,68.4,0.9,8,"152-10/KD",41588,"NPS-28410"]
[196,"FM-W 2.55 MODULKOLLEKTOR",39,2.358,0.791,3.74,0.0168,68.4,0.9,8,"139-10/KD",41588,"NPS-28710"]
[789,"fujisol fuji-c",124,1.626,0.644,1.5,0.01,144,0.89,29,"15 v.1 /DER-LECS/2008",42659,"NPS-27213"]
[26,"Gamelux-N",11,2.1,0.773,3.1,0.021,72,0.88,7,"8/DER-LECS/08",41398,"NPS 15111"]
[629,"GE H 2.0 C",99,1.81,0.791,4.5,0.021,129.6,0.96,6,"CA/RPT/4451/001/INTA/11",41333,"NPS-8211"]
[630,"GE H 2.5 C",99,2.32,0.791,4.5,0.021,129.6,0.96,6,"CA/RPT/4451/001/INTA/11",41333,"NPS-8311"]
[627,"GE V 2.0 C",99,1.824,0.729,4.884,0.011,79.2,0.92,9,"21210574_BC",41333,"NPS-8011"]
[628,"GE V 2.0 T",99,1.824,0.723,3.038,0.026,82.8,0.93,9,"21210574_VC",41333,"NPS-8111"]
[626,"GE V 2-0 A",99,1.824,0.728,4.632,0.0152,82.8,0.92,9,"21210574_P_C",41333,"NPS-7911"]
[566,"GF 100 NV",81,8.578,0.796,3.375,0.015,72,0.95,23,"2.01.00713.1.0-LT",41530,"NPS-39011"]
[567,"GF 120 NV",81,10.723,0.796,3.375,0.015,72,0.95,23,"2.01.00713.1.0-LT",41530,"NPS-39111"]
[564,"GF 50 NV",81,4.289,0.796,3.375,0.015,72,0.95,23,"2.01.00713.1.0-LT",41530,"NPS-38811"]
[568,"GF 55 NV",81,4.289,0.796,3.375,0.015,72,0.95,23,"2.01.00713.1.0-LT",41224,"NPS-28810"]
[565,"GF 70 NV",81,6.434,0.796,3.375,0.015,72,0.95,23,"2.01.00713.1.0-LT",41530,"NPS-38911"]
[570,"GF 70 NV",81,6.434,0.796,3.375,0.015,72,0.95,23,"2.01.00713.1.0-LT",41530,"NPS-38911"]
[569,"GF 75 NV",81,6.434,0.796,3.375,0.015,72,0.95,23,"2.01.00713.1.0-LT",41224,"NPS-28910"]
[539,"GK10AL",53,9.41,0.789,3.834,0.011,75,0.95,17,"2.04.00564.10-LT (2a)",41788,"NPS-22611"]
[350,"GK10AL",53,9.41,0.789,3.834,0.011,46.8,0.95,17,"2.04.00.564",41778,"NPS-22611"]
[824,"GK10-AL-HP",53,9.28,0.809,2.858,0.015,72,0.95,9,"21218595a_EN_P_GK3501_FL / 21218595s_EN_R_GK3501_F",42496,"NPS - 19014"]
[538,"GK5AL",53,4.665,0.789,3.834,0.011,75,0.95,17,"2.04.00564.10-LT (2a)",41788,"NPS-22511"]
[351,"GK5AL",53,4.665,0.789,3.834,0.011,936,0.95,17,"2.04.00.564",41778,"NPS-22511"]
[823,"GK5-AL-HP",53,4.642,0.809,2.858,0.015,72,0.95,9,"21218595a_EN_P_GK3501_FL / 21218595s_EN_R_GK3501_F",42496,"NPS - 18914"]
[522,"Greemheiss GH - AS 24 V",76,2.35,0.759,4.241,0.0033,60,0.91,4,"KTB-2008-47",41416,"NPS-22310"]
[520,"Greenheiss GH - AS 18 V",76,1.767,0.748,3.718,0.0141,46.8,0.92,3,"30.109.0-2-1",41416,"NPS-22110"]
[521,"Greenheiss GH - AS 20 V",76,1.96,0.759,4.241,0.0033,60,0.91,4,"KTB-2008-47",41416,"NPS-22210"]
[523,"Greenheiss GH - AS 26 V",76,2.514,0.759,4.241,0.0033,46.8,0.95,3,"30.1096.0-3-1",41416,"NPS-22410"]
[525,"Greenheiss GH - ECO 18 V",76,1.77,0.746,4.57,0.012,68.4,0.94,3,"30.1401.0-3-1",42112,"NPS-21211"]
[526,"Greenheiss GH - ECO 20 V",76,1.96,0.756,4.887,0.009,68.4,0.94,3,"30.1401.0-3-1",42112,"NPS-21311"]
[529,"Greenheiss GH - NEO 18 V",76,1.77,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",42112,"NPS-21611"]
[530,"Greenheiss GH - NEO 20 V",76,1.96,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42112,"NPS-21711"]
[531,"Greenheiss GH - NEO 24 V",76,2.41,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42112,"NPS-21811"]
[532,"Greenheiss GH - NEO 26 V",76,2.49,0.769,3.957,0.01,72,0.94,3,"30.1520.0-3-1",42112,"NPS - 15413"]
[527,"Greenheiss GH - TOP 20 V",76,2,0.792,3.722,0.018,176.4,0.94,3,"30.1520.0-4-1",42112,"NPS-21411"]
[528,"Greenheiss GH - TOP 24 V",76,2.3,0.797,3.756,0.016,176.4,0.94,3,"30.1520.0-6-1",42112,"NPS-21511"]
[524,"Greenheiss GH -AS 26 H",76,2.497,0.759,4.241,0.0033,70,0.94,4,"KTB-2009-16",41390,"NPS-22010"]
[686,"Heleos SCM 12",115,0.964,0.795,1.985,0.0117,84,1.2369,4,"KTB Nr. 2007-41-a-en",42109,"NPS-34711"]
[687,"Heleos SCM 15",115,1.204,0.795,1.985,0.0117,84,1.2369,4,"KTB Nr. 2007-41-a-en",42109,"NPS-34811"]
[688,"Heleos SCM 20",115,1.603,0.795,1.985,0.0117,84,1.2369,4,"KTB Nr. 2007-41-a-en",42109,"NPS-34911"]
[838,"Helioplan DB",152,2.4,0.7888,3.26,0.015,75.6,0.98,9,"21218501_EN_P_FK8250N4M",42462,"GPS-8542"]
[837,"Helioplan S",152,2.404,0.785,3.594,0.014,72,0.98,23,"2.04.00834.1.0-1 QT",42302,"GPS-8527"]
[919,"Helioplan S mini",152,1.924,0.759,3.48,0.0161,72,0.95,16,"2006-35-K-EN",43022,"GPS-8588"]
[186,"HELIOSTAR 218 S4 STECK",23,1.97,0.765,3.65,0.0126,50,0.94,8,"42-09/KD",43446,"NPS-29616"]
[185,"HELIOSTAR 252 S4 STECK",23,2.291,0.779,3.56,0.0146,50,0.95,8,"87-06/D",43355,"NPS-25116"]
[689,"HIYASU ADVANCE 1.5.",116,1.38,0.725,3.509,0.015,72,0.82,5,"10COL973Q, 10COL972 y 10COL973",41755,"GPS-8481"]
[690,"HIYASU ADVANCE 1.8.",116,1.7,0.725,3.509,0.015,72,0.82,5,"10COL973Q, 10COL972 y 10COL973",41755,"GPS-8481"]
[691,"HIYASU ADVANCE 2.0.",116,1.86,0.725,3.509,0.015,72,0.82,5,"10COL973Q, 10COL972 y 10COL973",41755,"GPS-8481"]
[692,"HIYASU ADVANCE 2.5.",116,2.23,0.725,3.509,0.015,72,0.82,5,"10COL973Q, 10COL972 y 10COL973",41755,"GPS-8481"]
[693,"HIYASU ADVANCE 2.7.",116,2.57,0.725,3.509,0.015,72,0.82,5,"10COL973Q, 10COL972 y 10COL973",41755,"GPS-8481"]
[615,"HUCUSOL 10833-VP",98,2.012,0.741,3.9,0.008,150,0.95,2,"C1341",41333,"NPS-37211"]
[613,"HUCUSOL 1083-VP",98,1.987,0.724,4.442,0.013,150,0.95,17,"2.04.00680.1.0-1-QT",41333,"NPS-6811"]
[617,"HUCUSOL 10844-VP",98,1.988,0.785,3.671,0.01,180,0.95,17,"2.04.00680.1.0-3 LT",41333,"NPS-7311"]
[616,"HUCUSOL 1084-VP",98,1.988,0.737,3.995,0.013,180,0.95,17,"2.04.00680.1.0-2 LT",41333,"NPS.6911"]
[618,"HUCUSOL 1093-VP",98,1.989,0.733,4.3,0.015,144,0.95,17,"2.04.00680.1.0-4 LT",41333,"NPS-7011"]
[620,"HUCUSOL 10944-VP",98,1.99,0.796,3.578,0.012,180,0.95,17,"2.04.00680.1.0-7 LT",41333,"NPS-7411"]
[619,"HUCUSOL 1094-VP",98,1.988,0.746,6.538,0.002,144,0.95,17,"2.04.00680.1.0-5 LT",41333,"NPS-7111"]
[621,"HUCUSOL 1095-VP",98,1.989,0.81,4.912,0.016,180,0.95,17,"2.04.00680.1.0-6 LT",41333,"NPS-7211"]
[624,"HUCUSOL 11000-VP",98,1.99,0.769,3.313,0.019,180,0.95,3,"30.0803.0-1",41333,"NPS-6411"]
[622,"HUCUSOL 1100-VP",98,1.991,0.811,3.968,0.009,180,0.95,17,"2.04.00680.1.0-1 LT",41333,"NPS-6711"]
[623,"HUCUSOL 1200-HP",98,1.989,0.8,3.612,0.033,180,0.95,17,"2.04.00609.1.0-2 LT",41333,"NPS-6611"]
[625,"HUCUSOL 21000-VP",98,1.99,0.745,3.423,0.027,180,0.95,3,"30.0803.1-1",41333,"NPS-6511"]
[667,"Icaro HF 2.3",108,2.21,0.737,3.775,0.018,126,0.89,9,"21211249a_HF2.3",42057,"NPS-3411"]
[665,"Icaro VF 2.0",108,1.87,0.755,3.72,0.017,126,0.89,9,"21211664a_VF2.0",42057,"NPS-3211"]
[666,"Icaro VF 2.3",108,2.21,0.75,3.706,0.009,126,0.89,9,"21210486a",42057,"NPS-3311"]
[668,"Icaro VF 2.8",108,2.657,0.771,3.24,0.026,126,0.89,9,"21211664a_VF2.8",42057,"NPS-3511"]
[537,"IDMK 25 AL",53,2.33,0.776,3.293,0.011,72,0.94,5,"09COL784",41777,"NPS-22411"]
[536,"IDMK12 AL",53,1.11,0.765,3.951,0.011,72,0.92,5,"09COL785",41777,"NPS-22311"]
[352,"IDMK25",53,2.32,0.78,3.796,0.013,72,0.93,3,"Arsenal Research 2.04.00217.1.0",41280,"NPS-15009"]
[572,"Ingesol-AR",83,1.94,0.743,3.98,0.0071,72,0.91,19,"EL008-09",43442,"NPS-29016"]
[435,"IS-PRO 1Q",63,0.8,0.758,5.9,0.011,85.5,0.92,7,"5a/101.104/2005",42104,"GPS-8192"]
[433,"IS-PRO 2H",63,1.995,0.789,4.42,0.0082,75,0.93,2,"C1130",41103,"GPS-8413"]
[434,"IS-PRO 2Q",63,1.995,0.771,4.68,0.0071,75,0.92,2,"C1131",41301,"GPS-8439"]
[432,"IS-TOP",63,2.007,0.765,4.24,0.0034,75,0.94,2,"C1119",41035,"GPS-8402"]
[860,"JEN/PPTT",164,2.06,0.789,3.673,0.016,72,0.95,3,"30.0827.0-1",42399,"NPS-114"]
[892,"Junkers FKT-2S",169,2.426,0.794,3.863,0.013,72,0.94,9,"21221193_EN_Bosch",43115,"NPS-35015"]
[908,"Junkers FKT-2W",169,2.426,0.802,3.833,0.015,72,0.94,9,"21222048_EN_Bosch",43115,"NPS-35115"]
[449,"KAIROS CF 2.0",65,1.82,0.7385,4.0045,0.0122,82.76,0.94,25,"1712-3/06/08/pv",41895,"GPS-8253"]
[451,"KAIROS XP 2.5 H",65,2.259,0.791,2.717,0.032,91.53,0.95,9,"21211914_SOLATRON S2,5H",41761,"GPS-8462"]
[450,"KAIROS XP 2.5 V",65,2.259,0.791,3.104,0.022,84.06,0.926,9,"21211914a_S2,5V",41757,"GPS-8461"]
[905,"Kingspan FPW 18",172,1.62,0.792,3.785,0.012,72,0.934,5,"12COL1078OEM06;12COL1079OEM06;12COL1079QOEM06.",43231,"NPS-20416"]
[906,"Kingspan FPW 21",172,1.92,0.792,3.785,0.012,72,0.934,5,"12COL1078OEM06;12COL1079OEM06;12COL1079QOEM06.",43231,"NPS-20516"]
[907,"Kingspan FPW 25",172,2.23,0.785,3.722,0.012,72,0.951,5,"12COL1078OEM06;12COL1079OEM06;12COL1079QOEM06.",43231,"NSP-20616"]
[902,"Kingspan VARISOL DF",172,1.054,0.783,1.061,0.023,65.16,0.967,9,"21212126_P;21212126_R",43232,"NSP-20816"]
[904,"Kingspan VARISOL HP 135",172,1.06,0.78,2.112,0.006,93.6,0.97,9,"21218850_EN_P_HP90;21218850_EN_P1_HP135;21218850a_",43232,"NPS-20116"]
[903,"Kingspan VARISOL HP 90",172,3.19,0.76,1.621,0.008,72,0.97,9,"21218850_EN_P_HP90;21218850_EN_P1_HP135;21218850a_",43232,"NPS-20016"]
[800,"LAMBORGHINI Tevere VRFA 2.0",107,1.89,0.76,3.656,0.016,72,0.87,9,"21221972_R_VMFA, 21221972 P VMFA",42418,"NPS-6614"]
[801,"LAMBORGHINI Tevere VRFA 2.3",107,2.226,0.76,3.656,0.016,72,0.87,9,"21221972_R_VMFA, 21221972 P VMFA",42418,"NPS-6714"]
[803,"LAMBORGHINI Tevere VRFA 2.8",107,2.69,0.768,3.591,0.016,72,0.87,9,"21221972_R_VMFA, 21221972 P VMFA",42418,"NPS-6814"]
[209,"LASIAN CLIMASOL V",43,2.03,0.819,4.227,0.014,72,0.9,3,"30.0194.0-1",41088,"NPS 17010"]
[141,"LBM 10 AR",43,10.1,0.838,3.774,0.012,72,0.97,3,"30.1042.0-2",41872,"NPS - 4811"]
[134,"LBM 10 HTF",43,10.1,0.83,3.523,0.015,72,0.92,3,"30.1154.0-2",41515,"NPS-28311"]
[146,"LBM 2 AR",43,2.02,0.838,3.774,0.012,72,0.97,3,"30.1042.0-2",41872,"NPS - 4411"]
[142,"LBM 2 HTF",43,2.01,0.83,3.523,0.015,72,0.92,3,"3011540-2",41810,"NPS-27911"]
[138,"LBM 4 AR",43,4.05,0.838,3.774,0.012,72,0.97,3,"3010420-2",41872,"NPS - 4511"]
[170,"LBM 4 HTF",43,4.05,0.83,3.523,0.015,72,0.92,3,"3011540-2",41810,"NPS-28011"]
[200,"LBM 4 HTF",43,4.05,0.83,3.523,0.015,72,0.92,3,"3011540-2",41279,"NPS-14109"]
[145,"LBM 6 AR",43,6.1,0.838,3.774,0.012,72,0.97,3,"30.1042.0-2",41872,"NPS - 6012"]
[144,"LBM 6 HTF",43,6.1,0.83,3.523,0.015,72,0.92,3,"3011540-2",41810,"NPS-28111"]
[135,"LBM 8 AR",43,8.1,0.838,3.774,0.012,72,0.97,3,"30.1042.0-2",41587,"NPS - 4711"]
[136,"LBM 8 HTF",43,8.1,0.83,3.523,0.015,40,0.92,3,"30.1154.0-2",41810,"NPS-28211"]
[893,"LBMG 13AR",43,13.17,0.803,2.888,0.012,25,0.91,5,"15COL1257",43066,"NPS-32015"]
[895,"LBMG 13AR2",43,13.17,0.763,1.969,0.015,25,0.91,5,"15COL1247",43069,"NPS-33215"]
[894,"LBMG 8AR",43,7.91,0.803,2.888,0.012,25,0.91,5,"15COL1257",43066,"NPS-31915"]
[896,"LBMG 8AR2",43,7.91,0.763,1.969,0.015,25,0.91,5,"15COL1247",43069,"Nps-33115"]
[573,"LKN 90L",84,1.6,0.623,3.956,0.01,72,0.95,3,"30.0164.0-1",41420,"GPS-8133"]
[574,"LKN 90LTi",84,1.6,0.65,3.894,0.019,72,0.99,3,"30.0164.1-1",41420,"GPS-8135"]
[577,"LKN LA 180 Ti",84,1.84,0.814,4.061,0.013,72.01,0.98,23,"2.04.00750.1.0-2-QT",41558,"GPS-8469"]
[575,"LKN LH 26 Ti",84,2.56,0.694,4.187,0.01,68.4,0.96,3,"30.0164.2-1",41420,"GPS-8134"]
[576,"LKN SP-400",84,2.153,0.773,1.43,0.0059,74.85,0.88,8,"106-06/D",41207,"NPS-27710"]
[578,"LKN SP-500",84,3.228,0.779,1.07,0.0135,74.5,0.9,8,"107-06/D",41207,"NPS-27810"]
[788,"LP-SUN 20",88,2,0.784,4.083,0.016,190.8,0.94,3,"30.1678.0-1-1",42659,"NPS-45211"]
[736,"LUM-2500",185,2.58,0.797,3.689,0.012,72,0.95,3,"30.1761.0-3-1",42988,"NPS-24315"]
[178,"MEDITERRANEO 200",4,1.89,0.756,4.305,0.009,74,0.93,3,"30.1193.0-1-1",41561,"GPS-8421"]
[177,"MEDITERRANEO 250",4,2.37,0.773,3.818,0.014,74,0.93,3,"CA/RPT/4451/001/INTA/11",41561,"GPS-8421"]
[971,"Megasun ST 2500 Selectivo",199,2.32,0.7671,3.7479,0.0147,72,0.95,3,"30.0012.0-3 Anexo 7, 30.0012.0-3 Anexo 6",44169,"NPS-21618"]
[502,"Mes ALW 2.0",72,2,0.792,3.722,0.018,176.4,0.94,3,"30.1520.0-4-1",41329,"NPS-14411"]
[503,"Mes ALW 2.4",72,2.3,0.792,3.756,0.018,176.4,0.94,3,"30.1520.0-6-1",41329,"NPS-14511"]
[34,"ML 2.0 Tinox",15,1.84,0.772,3.2,0.042,72,0.85,6,"CA/RPT/4451/006/INTA/09",42378,"NPS-48713"]
[826,"ML 2700",15,2.7,0.823,3.86,0,72,0.88,6,"CA/RPT/4451/013/INTA/11-1",42403,"NPS 1714"]
[33,"ML 3.0 Tinox",15,2.67,0.754,2.9,0.052,72.8,0.85,6,"CA/RPT/4451/008/INTA/09",42356,"NPS-48613"]
[35,"ML-2.4 SH Tinox Horizontal",15,2.44,0.756,3.9,0.028,72,0.85,6,"CA/RPT/4451/019/INTA/08",42403,"NPS-2614"]
[600,"MNE 01",94,1.995,0.696,6.2083,0.0094,68.5,0.912,26,"KT08-06I, II",41603,"NPS-51111"]
[596,"MNE 03",94,2.266,0.696,6.2083,0.0094,68.5,0.912,26,"KT08-06I, II",41603,"NPS-50711"]
[597,"MNE 04",94,1.613,0.696,6.2083,0.0094,68.5,0.912,26,"KT08-06I, II",41603,"NPS-50811"]
[598,"MNE 16",94,1.302,0.721,5.8355,0.0264,72.2,0.878,26,"KT08-05I",41603,"NPS-50911"]
[599,"MNE 20",94,1.768,0.696,6.2083,0.0094,68.5,0.912,26,"KT08-06I, II",41603,"NPS-51011"]
[674,"Nagaterm NT 215 A",112,2.15,0.789,2.9,0.006,71.5,0.95,6,"CA/RPT/4451/005/INTA/10",41812,"NPS-24812"]
[296,"NEO 18",3,1.77,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",42050,"NPS-5511"]
[297,"NEO 20",3,2,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42050,"NPS-5611"]
[298,"NEO 20H",3,2.13,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",42050,"NPS-5711"]
[299,"NEO 20M",3,1.96,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42050,"NPS-5811"]
[300,"NEO 21",3,2.08,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42050,"NPS-5911"]
[301,"NEO 24",3,2.41,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42050,"NPS-6011"]
[302,"NEO 26",3,2.49,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42050,"NPS-6111"]
[608,"NEO 26H",3,2.49,0.769,3.957,0.01,72,0.94,3,"30.1520.0-3-1",42050,"NPS-42811"]
[816,"NEO20MH",3,1.96,0.769,3.957,0.01,68.4,0.94,3,"30.2148.0",42050,"NPS-13113"]
[184,"NEOS",4,1.924,0.794,3.639,0.017,76.1,0.95,4,"2006-35-a-en-k",41392,"GPS-8174"]
[504,"Nou ALW 1.8",72,1.77,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",41329,"NPS-14611"]
[505,"Nou ALW 2.0",72,1.96,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",41329,"NPS-14711"]
[506,"Nou ALW 2.4",72,2.41,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",41329,"NPS-14811"]
[507,"Nou ALW 2.6",72,2.49,0.769,3.957,0.01,72,0.94,3,"30.1520.0-3-1",41329,"NPS-14911"]
[776,"Novasol HSTi 2200",153,2,0.82,3.734,0.018,72,0.93,3,"078/000027",41665,"NPS - 5912"]
[777,"Novasol HSTi 2600",153,2.32,0.81,3.683,0.017,72,0.93,3,"078/000027",41665,"NPS - 6012"]
[772,"Novasol HTTi 2200",153,2,0.778,3.911,0.01,72,0.95,3,"078/000029",41665,"NPS - 5512"]
[773,"Novasol HTTi 2600",153,2.32,0.77,3.442,0.016,72,0.95,3,"078/000029",41665,"NPS - 5612"]
[774,"Novasol VSTi 2200",153,1.99,0.82,3.734,0.018,72,0.93,3,"078/000027",41665,"NPS - 5712"]
[775,"Novasol VSTi 2600",153,2.32,0.81,3.683,0.017,72,0.93,3,"078/000027",41665,"NPS - 5812"]
[770,"Novasol VTTi 2200",153,2,0.778,3.911,0.01,72,0.95,3,"078/000029",41665,"NPS - 5312"]
[771,"Novasol VTTi 2600",153,2.32,0.7,3.442,0.016,72,0.95,3,"078/000029",41665,"NPS - 5412"]
[480,"NT 1010",69,2,0.792,3.722,0.018,176.4,0.94,3,"30.1520.0-4-1",42059,"NPS - 9413"]
[481,"NT 1208",69,2.3,0.797,3.756,0.016,176.4,0.94,3,"30.1520.0-6-1",42059,"NPS - 9513"]
[954,"Openplus OP-V2",190,2.01,0.741,3.3,0.012,75,0.88,16,"KTB Nr. 2009-04-k",43446,"NPS-12515"]
[320,"PA-D",50,1.87,0.801,3.195,0.016,72,0.89,3,"30,1761",43709,"NPS-17217"]
[321,"PA-E",50,2.16,0.797,3.689,0.012,72,0.89,3,"30,1761",43717,"NPS-17017"]
[322,"PA-F",50,2.58,0.801,3.195,0.016,72,0.95,3,"30,1761",43709,"NPS-17117"]
[806,"PA-G",50,2.58,0.722,3.39,0.014,72,0.86,3,"30,2399",43190,"NPS-15916"]
[804,"PA-H",50,1.87,0.75,3.951,0.008,72,0.86,3,"30,2399",43190,"NPS-15716"]
[805,"PA-I",50,2.17,0.75,3.951,0.008,72,0.86,3,"30,2399",43190,"NPS-15816"]
[925,"PFM S 2.01",187,2.01,0.75,3.829,0.013,72,0.87,5,"011-7S2393 F",43427,"NPS-31516"]
[927,"PFM S 2.55",187,2.55,0.77,3.657,0.015,72,0.87,5,"011-7S2395 F",43427,"NPS-31716"]
[929,"PFM S 3.30",187,3.32,0.77,3.772,0.014,72,0.85,5,"011-7S2397 F",43427,"NPS-31916"]
[926,"PFM W 2.01",187,2.01,0.76,4.244,0.007,72,0.91,5,"011-7S2394F",43427,"NPS-31616"]
[928,"PFM W 2.55",187,2.55,0.76,4.244,0.007,72,0.91,5,"011-7S2396 F",43427,"NPS-31816"]
[930,"PFM W 3.30",187,3.32,0.76,4.244,0.007,72,0.91,5,"011-7S2398 F",43427,"NPS-32016"]
[491,"Plan 1.8",71,1.767,0.748,3.718,0.0141,46.8,0.92,3,"30.109.0-2-1",41416,"NPS-7610"]
[492,"Plan 2",71,1.96,0.749,3.708,0.0136,60,0.91,4,"KTB-2008-47",41416,"NPS-7710"]
[493,"Plan 2.4",71,2.35,0.749,3.708,0.0136,60,0.91,4,"KTB-2008-47",41416,"NPS-7810"]
[490,"Plan 2.6",71,2.497,0.759,4.241,0.0033,70,0.94,4,"KTB-2009-16",41390,"NPS-7510"]
[494,"Plan 2.6M",71,2.514,0.749,3.708,0.0136,46.8,0.95,3,"30.1096.0-3-1",41416,"NPS-7910"]
[985,"PR-D",50,2.02,0.684,3.42,0.007,72,0.92,3,"30.3300.0R",44451,"NPS-7619"]
[986,"PR-E",50,2.33,0.684,3.42,0.007,72,0.92,3,"30.3300.0R",44451,"NPS-7719"]
[987,"PR-F",50,2.77,0.701,3.05,0.011,71,0.93,3,"30.3300.0R",44451,"NPS-7819"]
[984,"PR-K",50,1.66,0.684,3.42,0.007,72,0.92,3,"30.3300.0R",44451,"NPS-7519"]
[583,"Promasol Titanio V-1",179,1.87,0.772,4.862,0.005,61.2,0.84,3,"30.1317.0-1-2",41671,"NPS-7512"]
[582,"Promasol V-1",179,1.87,0.693,6.322,0.019,61.2,0.9,3,"30.1084.0-1-2",41671,"NPS-7412"]
[948,"PROMASUN 1.5 BLUE",179,1.4,0.73,3.75,0.015,72,0.85,20,"4077DE5",43177,"NPS-25216"]
[947,"PROMASUN 2.0 BLUE",179,1.88,0.73,3.75,0.015,72,0.85,20,"4085DQ1,4077DE1,4079DE1,4087DQ1, 4081DE1,4083DE1",43231,"NPS-19216"]
[949,"PROMASUN 2.6",179,2.37,0.72,3.45,0.024,72,0.86,20,"4083DE4",43231,"NPS-18916"]
[916,"PROMASUN 2.6 BLUE",179,2.37,0.76,3.67,0.015,72,0.85,20,"4004,4008,4003S,4003L, 4062DE2,4063",43236,"NPS-19316"]
[183,"PS 2.0",4,1.92,0.79,3.313,0.026,205,0.98,3,"30.0240.9",41364,"GPS-8180"]
[852,"PSH20",87,1.99,0.788,3.911,0.01,72,0.94,3,"30.1699.0",42400,"NPS-23614"]
[853,"PSH25",87,2.32,0.788,3.911,0.01,72,0.94,3,"30.1699.0",42400,"NPS-23814"]
[850,"PSV20",87,1.99,0.788,3.911,0.01,72,0.94,3,"30.1699.0",42400,"NPS-23514"]
[851,"PSV25",87,2.32,0.788,3.911,0.01,72,0.94,3,"30.1699.0",42400,"NPS-23714"]
[180,"PSXL",4,4.665,0.789,3.834,0.011,40,0.95,23,"2.04.00564.1.0-LT",41678,"GPS-8279"]
[179,"PSXXL",4,9.43,0.789,3.834,0.011,40,0.95,23,"2.04.00564.1.0-LT",41678,"GPS-8279"]
[808,"QA-D",50,2.02,0.647,3.93,0.007,72,0.93,3,"30.3300.2R",44451,"NPS-6819"]
[809,"QA-E",50,2.33,0.647,3.93,0.007,72,0.93,3,"30.3300.2R",44451,"NPS-6919"]
[810,"QA-F",50,2.76,0.651,3.34,0.011,72,0.93,3,"30.3300.2R",44451,"NPS-7019"]
[807,"QA-K",50,1.66,0.647,3.93,0.007,72,0.86,3,"30.3300.2R",44451,"NPS-6719"]
[324,"QR-D",50,2.02,0.683,3.772,0.013,72,0.93,3,"30.3300.3R",44451,"NPS-7219"]
[325,"QR-E",50,2.33,0.683,3.772,0.013,72,0.93,3,"30.3300.3R",44451,"NPS-7319"]
[326,"QR-F",50,2.77,0.703,3.51,0.014,71,0.94,3,"30.3300.3R",44451,"NPS-7419"]
[323,"QR-K",50,1.66,0.683,3.772,0.013,72,0.93,3,"30.3300.3R",44451,"NPS-7119"]
[45,"Reisol R42000 U",19,1.97,0.795,3.722,0.014,72,0.97,3,"30.0288.1-4",41236,"NPS-31610"]
[190,"S-21",29,2.16,0.746,2.155,0.042,72,0.92,6,"CA/RPT/4451/001/INTA/08",41165,"NPS-23410"]
[959,"Saclima E-21",194,1.92,0.785,3.722,0.012,72,0.951,5,"12COL1079, 12COL1079Q",43411,"NPS-26916"]
[961,"Saclima EH-21",194,1.92,0.785,3.722,0.012,72,0.951,5,"12COL1079, 12COL1079Q",43547,"NPS-7617"]
[960,"Saclima L-21",194,2.23,0.785,3.722,0.012,72,0.951,5,"12COL1079, 12COL1079Q",43411,"NPS-26816"]
[962,"Saclima LH-21",194,2.23,0.785,3.722,0.012,72,0.951,5,"12COL1079, 12COL1079Q",43547,"NPS-7717"]
[607,"SCE 250 CU",53,2.392,0.759,3.48,0.0161,72,0.95,4,"2006-35-b-en",41734,"NPS-17311"]
[909,"SCE202-M",53,1.922,0.755,3.745,0.015,72,0.96,4,"KTB Nr.: 2013-09",43122,"NPS-36215"]
[349,"SCE250",53,2.392,0.759,3.48,0.161,604.8,0.95,4,"2006-35-A",41827,"NPS-29311"]
[346,"SCHUCOSOL G U.5",26,2.47,0.798,2.275,0.022,72,0.906,11,"30.0240.6-1",41161,"NPS-22510"]
[59,"SCV 2.3",24,2.352,0.729,2.804,0.055,48.97,0.92,9,"21209076_SD_SCV23",43083,"NPS-34215"]
[201,"SECUPIPE CPC 1",43,1,0.642,0.885,0.001,60,0.94,5,"06COL513/1",41006,"NPS-6510"]
[202,"SECUPIPE CPC 2",43,1.99,0.642,0.885,0.001,60,0.94,5,"06COL513/1",41006,"NPS-6710"]
[204,"SECUPIPE CPCI 1",43,1,0.642,0.885,0.001,60,0.94,5,"06COL513/1",41006,"NPS-6610"]
[205,"SECUPIPE CPCi 2",43,1.99,0.642,0.885,0.001,60,0.94,5,"06COL513/1",41006,"NPS-6810"]
[206,"SECUPIPE CPCi 3",43,2.99,0.642,0.885,0.001,60,0.94,5,"06COL513/1",41006,"NPS-7010"]
[585,"SFK27",87,2.49,0.746,3.232,0.014,75,0.915,5,"06COL482/3OEM10D",41230,"GPS-8244"]
[640,"Sime plano 182",104,1.88,0.73,3.75,0.015,72,0.85,20,"4079DE1",41336,"NPS-8511"]
[641,"Sime plano 230",104,2.37,0.76,3.67,0.015,72,0.85,20,"4085DQ1",41336,"NPS-8611"]
[343,"SK 12 G",54,2.38,0.708,4.413,0.011,72,0.96,3,"30.1601.0-3-1",41538,"NPS-36911"]
[344,"SK 12 GH",54,2.38,0.708,4.413,0.011,72,0.94,3,"30,1601",41538,"NPS-37111"]
[342,"SK 12 H",54,2.08,0.708,4.413,0.011,72,0.94,3,"30.1601.0",41538,"NPS-37011"]
[533,"SK 400",53,1.88,0.741,3.705,0.015,160,0.923,5,"07COL577OEM05",41778,"NPS-22711"]
[329,"SK 500 L",53,2.307,0.799,3.659,0.005,133.2,0.95,17,"2.04.00335",41880,"NPS-36411"]
[341,"SK12",54,2.08,0.708,4.413,0.011,72,0.94,3,"30.1601.0-1-1",41538,"NPS-36811"]
[353,"SK500N",53,2.211,0.77,3.494,0.017,133.2,0.95,3,"2.04.0335.1.0-2",41827,"NPS-29411"]
[348,"SK500N4ECO",53,2.309,0.74,3.455,0.013,133.2,0.95,3,"30.0137.0",41827,"NPS-29511"]
[331,"SK500NECO",53,2.211,0.7,3.494,0.017,133.2,0.95,3,"30.0055.0-2",41911,"NPS-25710"]
[652,"SKN 4.0 S",49,2.25,0.766,3.216,0.015,82.8,0.92,9,"21216476_EN_Bosch",42109,"NPS-55211"]
[653,"SKN 4.0 W",49,2.25,0.77,3.871,0.012,82.8,0.92,9,"21218052_EN_Bosch",42109,"NPS-55011"]
[632,"SKR 12.1 R",49,2.57,0.644,0.749,0.005,61.2,0.98,5,"06COL456OE M07",42109,"NPS-2612"]
[534,"SKR 500",53,2.26,0.82,3.821,0.0108,50,0.96,4,"2010-08-k-a",42755,"NPS-115"]
[535,"SKR 500 L",53,2.26,0.794,3.514,0.0147,50,0.96,4,"2010-09-k-a",41899,"NPS-23510"]
[631,"SKR 6.1 R",49,1.28,0.644,0.749,0.005,61.2,0.98,5,"06COL456OE M06",42109,"NPS-2612"]
[249,"SKS 4.0 S",49,2.08,0.851,4.036,0.0108,72,0.95,4,"2066-30",42050,"NPS-49311"]
[250,"SKS 4.0 W",49,2.08,0.851,4.036,0.0108,72,0.95,4,"30/31/2066",42050,"NPS-49411"]
[587,"SMK12",87,1.84,0.724,3.687,0.012,50,0.92,5,"05COL423/1",41510,"GPS-8194"]
[175,"SOL 200",4,1.887,0.804,3.75,0.014,74.192,0.94,4,"2011-25",41926,"GPS-8417"]
[453,"SOL 2000",66,1.77,0.746,4.45,0.012,68.4,0.94,3,"30.1401.0-3-1",41225,"NPS-35611"]
[457,"SOL 2000 S",66,1.77,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",41329,"NPS-36011"]
[176,"SOL 200H",4,1.877,0.824,3.974,0.015,74.587,0.94,4,"2011-26",41926,"GPS-8420"]
[454,"SOL 2200",66,1.96,0.756,4.887,0.009,68.4,0.94,3,"30.1401.0-3-1",41225,"NPS-35711"]
[458,"SOL 2200 S",66,1.96,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",41329,"NPS-36111"]
[455,"SOL 2200 ST",66,2,0.792,3.722,0.018,176.4,0.94,3,"30.1520.0-4-1",41329,"NPS-35811"]
[173,"SOL 250",4,2.354,0.821,3.669,0.009,73.5,0.93,4,"2010-31-K",42318,"GPS-8449"]
[456,"SOL 2500 ST",66,2.3,0.797,3.756,0.016,176.4,0.94,3,"30.1520.0-6-1",41329,"NPS-35911"]
[174,"SOL 250H",4,2.354,0.819,3.671,0.0129,73.06,0.94,4,"2010-31-K",42071,"GPS-8450"]
[459,"SOL 2600 S",66,2.41,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",41329,"NPS-36211"]
[460,"SOL 2700 S",66,2.49,0.769,3.957,0.01,72,0.94,3,"30.1520.0-3-1",41329,"NPS-36311"]
[452,"SOL 2700 SH",66,2.497,0.759,4.241,0.0033,70,0.94,4,"KTB-2009-16",41390,"NPS-35511"]
[244,"SOLAR ENERGY RK 2000 ALPIN",155,1.924,0.759,3.48,0.0161,76,0.95,24,"2006-35-K-EN",41628,"GPS-8472"]
[245,"SOLAR ENERGY RK 2300 ALPIN",155,2.22,0.759,3.48,0.0161,76,0.95,24,"2006-35-K-EN",41628,"GPS-8472"]
[609,"SOLAR ENERGY RK 2500 ALPIN",155,2.392,0.759,3.48,0.0161,76,0.95,24,"2006-35-K-EN",41628,"GPS-8472"]
[854,"SOLAR ENERGY RK2001M",155,1.922,0.755,3.745,0.015,72.84,0.96,24,"KTB-2013-09-b",42463,"GPS-8543"]
[855,"SOLAR ENERGY RK2301M",155,2.236,0.757,3.501,0.0172,72,0.97,24,"KTB-2012-09",42463,"GPS-8544"]
[856,"SOLAR ENERGY RKE 2500",155,2.35,0.808,3.745,0.01,72,0.96,9,"21218501_EN_P_FK8257N4M_FL",42548,"GPS-8486"]
[858,"SOLAR ENERGY RKE 2501",155,2.34,0.815,3.454,0.018,72,0.93,5,"12COL1140OEM02",42678,"GPS-8556"]
[857,"SOLAR ENERGY RKEQ 2500 H",155,2.346,0.808,3.279,0.017,72,0.96,9,"21218491_EN_P1_FK8257L4M_FL",42548,"GPS-8485"]
[610,"SOLAR ENERGY RKQ 2000 ALPIN",155,1.91,0.759,3.48,0.0161,76,0.95,24,"2006-35-K-EN",41628,"GPS-8472"]
[611,"SOLAR ENERGY RKQ 2300 ALPIN",155,2.14,0.759,3.48,0.0161,76,0.95,24,"2006-35-K-EN",41628,"GPS-8472"]
[876,"SOLAR ENERGY RKQ 2300 H",155,2.23,0.759,3.48,0.016,76,0.95,24,"2006-35-K-EN",42376,"GPS-8472"]
[612,"SOLAR ENERGY RKQ 2500 ALPIN",155,2.39,0.759,3.8,0.0161,76,0.95,24,"2006-35-K-EN",41628,"GPS-8472"]
[877,"SOLAR ENERGY RKQ 2500 H",155,2.39,0.759,3.48,0.016,76,0.95,24,"2006-35-K-EN",42376,"GPS-8472"]
[347,"SOLAR ROOF AR",43,9.619,0.802,3.41,0.00108,61.13,0.91,8,"56-04/D 57-04/Q",41764,"NPS-21111"]
[218,"SOLARIA 2.1 AL AL",46,1.87,0.75,3.391,0.008,45,0.86,3,"CENER/ 30.1126.0-2-2",41420,"NPS-24011"]
[220,"SOLARIA 2.1 G AL",46,1.87,0.696,4.821,0.015,45,0.87,3,"CENER/ 30.1166.0-3-1",42109,"NPS-30911"]
[217,"SOLARIA 2.4 AL AL",46,2.17,0.722,3.39,0.014,45,0.86,3,"CENER/ 30.1126.0-2-2",41420,"NPS-24111"]
[221,"SOLARIA 2.4 G AL",46,2.17,0.693,4.39,0.018,45,0.87,3,"CENER/ 30.1166.0-3-1",42109,"NPS-31011"]
[219,"SOLARIA 2.8 AL AL",46,2.58,0.722,3.39,0.014,45,0.86,3,"CENER/ 30.1126.0-2-2",41420,"NPS-24211"]
[222,"SOLARIA 2.8 G AL",46,2.58,0.693,4.39,0.018,45,0.87,3,"CENER/ 30.1166.0-3-1",42109,"NPS-31111"]
[714,"Solaris CP L",55,2.3,0.72,3.45,0.024,72,0.85,20,"4087 DQ1 / 4083 DE1",42068,"NPS-7313"]
[345,"Solaris CP1",55,2,0.799,3.4,0.026,50,0.95,3,"30.0753.0-1",62415,"NPS -25613"]
[713,"Solaris CP1 L",55,2.3,0.76,3.67,0.015,72,0.85,20,"4087 DQ1 / 4079 DE1",42068,"NPS-7413"]
[711,"Solaris CP1 Nova",55,2,0.778,3.736,0.016,72,0.85,3,"30.1676.0-1-1/30.1676.0-2-1",42468,"NPS-14614"]
[712,"Solaris CP3",55,2,0.783,3.609,0.017,72,0.88,3,"30.1613.0-2-1/30.1716.0-1-1",42468,"NPS-12012"]
[715,"Solaris CP4 Nova L",55,2.354,0.821,3.669,0.009,72,0.93,3,"2010-30-K/30.1193.0-8-1",41325,"NPS-1113"]
[720,"Solaris LBM 10",55,10.1,0.83,3.523,0.015,72,0.92,3,"30.1154.0-2/30.1122.0-1-1",42257,"NPS-34313"]
[716,"Solaris LBM 2",55,2.01,0.83,3.523,0.015,72,0.92,3,"30.1154.0-2/30.1122.0-1-1",42257,"NPS-33913"]
[717,"Solaris LBM 4",55,4.05,0.83,3.523,0.015,72,0.92,3,"30.1154.0-2/30.1122.0-1-1",42257,"NPS-34013"]
[718,"Solaris LBM 6",55,6.1,0.83,3.523,0.015,72,0.92,3,"30.1154.0-2/30.1122.0-1-1",42257,"NPS-34113"]
[719,"Solaris LBM 8",55,8.1,0.83,3.523,0.015,72,0.92,3,"30.1154.0-2/30.1122.0-1-1",42257,"NPS-34213"]
[673,"Solcrafte RS1",110,1.84,0.814,4.061,0.013,144,0.98,23,"2.04.00786. 1.0-0T(1)",41794,"GPS-8484"]
[333,"Soliker 60 Basic",54,1.9,0.77,3.566,0.024,72,0.93,3,"30.0884.2-2",41686,"NPS-2611"]
[332,"Soliker 60 Plus",54,1.91,0.797,4.273,0.006,72,0.96,3,"30.0814.1-2",41730,"NPS-16911"]
[338,"Soliker EVO H Soliker",54,2.34,0.8,4.255,0.012,72,0.97,3,"30.1418.0-2-1",41644,"NPS-0111"]
[339,"Soliker Plus EVO",54,2.35,0.8,3.757,0.012,68.4,0.96,3,"30.1556.0-2-1",41553,"NPS-40111"]
[340,"Soliker Plus EVO M",54,2.06,0.817,3.976,0.015,72,0.89,3,"30.1288.0-2-1",41891,"NPS-22810"]
[337,"Soliker Plus G",54,2.37,0.783,3.512,0.021,133.2,0.94,3,"30.1555.0-3-1",41553,"NPS-40511"]
[336,"Soliker Plus GH",54,2.37,0.783,3.512,0.021,129.6,0.94,3,"30.1555.0",41553,"NPS-40411"]
[335,"Soliker Plus H",54,2.07,0.783,3.512,0.021,129.6,0.94,3,"30.1555.0",41553,"NPS-40311"]
[334,"SolikerPlus",54,2.04,0.782,3.569,0.02,129.6,0.94,3,"30.1555.0-1-1",41553,"NPS-40211"]
[509,"Soltherm 1.8",73,1.767,0.748,3.718,0.0141,46.8,0.92,3,"30.109.0-2-1",41416,"NPS-2310"]
[510,"Soltherm 2.0",73,1.96,0.749,3.708,0.0136,60,0.91,4,"KTB-2008-47",41416,"NPS-2410"]
[511,"Soltherm 2.4",73,2.35,0.749,3.708,0.0136,60,0.91,4,"KTB-2008-47",41416,"NPS-2510"]
[512,"Soltherm 2.6",73,2.514,0.749,3.708,0.0136,46.8,0.95,3,"30.1096.0-3-1",41416,"NPS-2610"]
[508,"Soltherm 2.6H",73,2.497,0.759,4.241,0.0033,70,0.94,4,"KTB-2009-16",41390,"NPS-2210"]
[482,"Soltherm ECO 1.8",70,1.77,0.746,4.57,0.012,68.4,0.94,3,"30.1401.0-3-1",41225,"NPS-15711"]
[483,"Soltherm ECO 2.0",70,1.96,0.756,4.887,0.009,68.4,0.94,3,"30.1401.0-3-1",41225,"NPS-15811"]
[486,"Soltherm NEO 1.8",70,1.77,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",41329,"NPS-16111"]
[487,"Soltherm NEO 2.0",70,1.96,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",41329,"NPS-16211"]
[488,"Soltherm NEO 2.4",70,2.41,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",41329,"NPS-16311"]
[489,"Soltherm NEO 2.6",70,2.49,0.769,3.957,0.01,72,0.94,3,"30.1520.0-3-1",41329,"NPS-16411"]
[484,"Soltherm TOP 2.0",70,2,0.792,3.772,0.018,176.4,0.94,3,"30.1520.0-4-1",41329,"NPS-15911"]
[485,"Soltherm TOP 2.4",70,2.3,0.797,3.756,0.016,176.4,0.94,3,"30.1520.0-6-1",41329,"NPS-16011"]
[841,"SOT-V2.5",154,2.25,0.78,3.477,0.018,169.2,0.95,11,"30.2067.0-2-1 R Anexo 6",42173,"NPS-24113"]
[785,"SP-18",123,1.62,0.792,3.785,0.012,72,0.934,5,"12COL1079 , 8 ,Q",42805,"NPS-6715"]
[786,"SP-21",123,1.89,0.785,3.722,0.0121,72,0.951,5,"12COL1079 , 8 ,Q",42805,"NPS-6815"]
[787,"SP-25",123,2.23,0.785,3.722,0.012,72,0.951,5,"12COL1079 , 8 ,Q",42805,"NPS-6915"]
[58,"SRD 2.3",24,2.352,0.801,3.761,0.012,52.04,0.8,9,"21209076_SD_SRD23",41540,"NPS-34415"]
[57,"SRH 2.3",24,2.352,0.801,3.32,0.023,53.57,0.82,9,"21209076_SD_SRH23",43083,"NPS-34515"]
[60,"SRV 2.3",24,2.352,0.79,2.4141,0.049,48.97,0.87,9,"21209076_SD_SRV23",43083,"NPS-34315"]
[584,"SSK21-4",87,1.92,0.744,4.187,0.005,36,0.956,5,"08COL689",41560,"GPS-8293"]
[592,"ST-2000",92,1.809,0.731,7.2,0.024,72,0.91,3,"30.0109.1-1",41195,"NPS-27210"]
[593,"ST-2000 S",92,1.78,0.763,3.9,0.007,72,0.9,3,"30.0109.0-1",41476,"NPS-2910"]
[594,"ST-2500",92,2.33,0.736,6.1,0.006,72,0.95,3,"30.0109.2-1",41195,"NPS-27310"]
[595,"ST-2500 S",92,2.3,0.7671,3.9,0.0147,72,0.86,3,"30.0012.0-3",41476,"NPS-3010"]
[586,"SUK27L",87,2.49,0.746,3.232,0.014,62,0.915,5,"06COL482/3OEM08D",41230,"GPS-8245"]
[862,"Sunnyline-28",148,2.48,0.747,3.4,0.016,183.1,0.93,14,"2.04.00360.1.0-2",42175,"NPS-24213"]
[931,"T1",186,0.79,0.663,5.765,0.041,90,0.95,11,"30.2603.0",43454,"NPS-29716"]
[463,"T11180",67,1.77,0.746,4.57,0.012,68.4,0.94,3,"30.1401.0-3-1",42045,"NPS-22911"]
[462,"T11200",67,1.96,0.756,4.887,0.009,68.4,0.94,3,"30.1401.0-3-1",42045,"NPS-23011"]
[466,"T12180",67,1.77,0.757,3.994,0.009,64.8,0.94,3,"30.1520.0-1-1",42045,"NPS-23311"]
[467,"T12200",67,1.96,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42045,"NPS-23411"]
[468,"T12240",67,2.41,0.769,3.957,0.01,64.8,0.94,3,"30.1520.0-1-1",42045,"NPS-23511"]
[469,"T12250",67,2.49,0.769,3.957,0.01,72,0.94,3,"30.1520.0-3-1",42045,"NPS-23611"]
[461,"T1225H",67,2.497,0.759,4.241,0.0033,70,0.94,4,"KTB-2009-16",42045,"NPS-22811"]
[465,"T13200",67,2,0.792,3.722,0.018,176.4,0.94,3,"30.1520.0-4-1",42045,"NPS-23111"]
[464,"T13240",67,2.3,0.797,3.756,0.016,176.4,0.94,3,"30.1520.0-6-1",42045,"NPS-23211"]
[579,"TAM-20-H",85,1.973,0.776,3.95,0.0165,40,0.93,8,"90-07/D",41755,"NPS-19111"]
[581,"TAM-20-V",85,1.969,0.775,3.73,0.0152,40,0.94,8,"88-07/D",41755,"NPS-19211"]
[580,"TAM-24-H",85,2.294,0.764,3.79,0.0168,40,0.93,8,"111-08/KD",41755,"NPS-19311"]
[993,"TERMICOL G21M",62,2.15,0.744,3.12,0.013,72,0.93,3,"30.3567.0-001",44478,"NPS-9619"]
[994,"TERMICOL G21MH",62,2.15,0.744,3.12,0.013,72,0.93,3,"30.3567.0-001",44478,"NPS -9719"]
[990,"TERMICOL G26M",62,2.56,0.731,3.36,0.01,72,0.93,3,"30.3567.0-003",44478,"NPS-9819"]
[992,"TERMICOL G26MH",62,2.56,0.731,3.36,0.01,72,0.93,3,"30.3567.0-003",43788,"NPS-9919"]
[991,"TERMICOL P21",62,2.29,0.685,3.15,0.006,72,0.92,3,"30.3567.0-003",44112,"NPS-17718"]
[671,"Tevere HF 2.3",109,2.21,0.737,3.775,0.018,126,0.89,9,"21211249a_HF2.3",42057,"NPS-3011"]
[669,"Tevere VF 2.0",109,1.87,0.755,3.72,0.017,126,0.89,9,"21211664a_VF2.0",42057,"NPS-2811"]
[670,"Tevere VF 2.3",109,2.21,0.75,3.706,0.009,126,0.89,9,"21210486a",42057,"NPS-2911"]
[672,"Tevere VF 2.8",109,2.657,0.771,3.24,0.026,126,0.89,9,"21211664a_VF2.8",42057,"NPS-3111"]
[363,"THERMOMAX DF 400-20",185,2.147,0.768,1.36,0.0053,72,0.99,8,"46-12/KD",42845,"NPS-10315"]
[364,"THERMOMAX DF 400-30",185,3.22,0.768,1.36,0.0053,72,0.99,8,"46-12/KD",42845,"NPS-10415"]
[366,"THERMOMAX HP 400-20",185,2.131,0.75,1.18,0.0095,72,0.99,8,"123-11/KD",43384,"NPS-16416"]
[367,"THERMOMAX HP 400-30",185,3.201,0.75,1.18,0.0095,72,0.99,8,"35-09/KD",43198,"NPS-16616"]
[369,"THERMOMAX HP 450-20",185,2.134,0.748,1.25,0.0071,72,0.99,8,"64-11/KD",43384,"NPS-16516"]
[370,"THERMOMAX HP 450-30",185,3.201,0.75,1.18,0.0095,72,0.99,8,"35-09/KD",43198,"NPS-16716"]
[371,"THERMOMAX VARISOL DF",185,1.054,0.783,1.061,0.023,65.16,0.967,9,"21212126_R",42775,"NPS-5515"]
[924,"THERMOMAX VARISOL HP135",185,1.06,0.78,2.112,0.006,93.6,0.97,9,"21218850_EN_PQ_HP135",43198,"NPS-16316"]
[923,"THERMOMAX VARISOL HP90",185,3.19,0.76,1.621,0.008,72,0.97,9,"21218850_EN_P",43198,"NPS-16216"]
[731,"Tisun FM S 2,55 Captador modular",39,2.36,0.823,3.797,0.014,68.4,0.9,23,"IET/401/2012",42022,"NPS-0613"]
[729,"Tisun FM S 2.00 Captador modular",39,1.839,0.803,3.872,0.014,68.4,0.9,23,"IET/401/2012",42022,"NPS-0413"]
[732,"Tisun FM W 2,55 Captador modular",39,2.36,0.823,3.797,0.014,68.4,0.9,23,"IET/401/2012",42022,"NPS-0713"]
[293,"TOP 20",3,2,0.792,3.722,0.018,176.4,0.94,3,"30.1520.0-4-1",42050,"NPS-5211"]
[294,"TOP 22",3,2.21,0.797,3.756,0.016,176.4,0.94,3,"30.1520.0-4-1",42050,"NPS-5311"]
[295,"TOP 24",3,2.3,0.797,3.756,0.016,176.4,0.94,3,"30.1520.0-6-1",42050,"NPS-5411"]
[216,"TOPSON F3-1",45,1.99,0.804,3.235,0.0117,76,0.94,4,"KTB 2007-32-K",42387,"NPS 1011"]
[215,"TOPSON F3-Q",45,2,0.794,3.494,0.015,87,0.954,9,"21209608",42387,"NPS-25911"]
[740,"TSV6",118,1.19,0.818,11.535,0.044,193.61,1.05,28,"291535",41740,"NPS-17912"]
[739,"TSV6.X",118,1.24,0.861,13.552,0.054,185.81,1.01,28,"299590",42173,"NPS-24513"]
[698,"UNISOL 60 BASIC",54,1.91,0.764,3.539,0.024,72,0.93,3,"30.0884.02-2",42043,"NPS-2611"]
[697,"Unisol 60 Plus",54,1.91,0.797,4.273,0.006,72,0.96,3,"30.0814.1-2",42043,"NPS-16911"]
[544,"VDF 15",77,1.58,0.816,2.735,0.0074,85.83,0.98,9,"21207819a",41165,"GPS-8225"]
[545,"VDF 20",77,2.12,0.821,2.824,0.0047,82.39,0.98,9,"21207819a",41165,"GPS-8224"]
[359,"VFK 125",183,2.352,0.753,3.936,0.017,53.87,0.92,9,"21209076a",43141,"NPS-3416"]
[950,"VFK 135 D",183,2.352,0.801,3.761,0.012,52,0.8,9,"21209076_135D",42994,"NPS-22315"]
[358,"VFK 135 VD",183,2.352,0.814,2.645,0.033,50.4,0.87,9,"2122067_EN_R y 2122067_EN_P",43446,"NPS-18417"]
[357,"VFK 145 H",183,2.352,0.801,3.32,0.023,54.1,0.82,9,"21209076 145 H",42994,"NPS-22515"]
[360,"VFK 145 V",57,2.352,0.79,2.414,0.049,49.5,0.87,9,"21209076 VFK 145 V",41553,"NPS-40811"]
[951,"VFK 145 V",183,2.352,0.79,2.414,0.049,48.97,0.87,9,"21209076_145V",42994,"NPS-22415"]
[267,"VITOSOL 100-F SH1B",42,2.237,0.753,4.14,0.0114,40,0.89,8,"41-09/KD",43231,"NPS-18716"]
[266,"VITOSOL 100-F SV1B",42,2.237,0.753,4.14,0.0114,40,0.89,8,"41-09/KD",43231,"NPS-18616"]
[936,"VITOSOL 100-FM SH1F",42,2.51,0.749,3.826,0.033,70,0.91,9,"21232812,002",43505,"NPS-2317"]
[934,"VITOSOL 100-FM SV1F",42,2.51,0.749,3.542,0.042,66,0.89,9,"21232812,001",43505,"NPS-2417"]
[937,"VITOSOL 100-FM SVKF",42,2.18,0.75,3.779,0.035,76,0.89,9,"21232812,003",43505,"NPS-2217"]
[932,"VITOSOL 200-FM SH2F",42,2.51,0.76,4.031,0.034,72,0.92,9,"21232810,002",43505,"NPS-2517"]
[933,"VITOSOL 200-FM SV2F",42,2.51,0.757,4.069,0.02,64,0.89,9,"21232810,001",43505,"NPS-2617"]
[938,"VITOSOL 200-T SP2A 1,26 m2",42,1.33,0.744,1.442,0.007,72,1,9,"21221633_EN_P_10H",43149,"NPS-8216"]
[939,"VITOSOL 200-T SP2A 1,51 m2",42,1.6,0.756,1.362,0.002,72,1,9,"21221633_EN_P_12V",43149,"NPS-8316"]
[940,"VITOSOL 200-T SP2A 3,03 m2",42,3.19,0.761,1.047,0.007,72,1,9,"21221633_EN_24V",43149,"NPS-8416"]
[941,"VITOSOL 200-T SPE 1.63 m2",42,1.73,0.66,1.33,0.0073,72,1,8,"115-12/KD",43150,"NPS-8616"]
[942,"VITOSOL 200-T SPE 3.26 m2",42,3.46,0.683,1.37,0.0041,72,1,8,"116-12/KD",43150,"NPS-8516"]
[973,"VITOSOL 300-TM SP3C 1.25 m2 HW",42,1.98,0.504,0.962,0.017,65,1.02,9,"21240359.001/002",43729,"NPS-19817"]
[974,"Vitosol 300-TM SP3C 1.51 m2",42,1.6,0.752,1.906,0.006,71.69,1.02,9,"21239899.001/002",43729,"NPS-19617"]
[972,"Vitosol 300-TM SP3C 3.03 m2",42,3.2,0.74,1.668,0.007,72.62,1.03,9,"21239899.001/002",43729,"NPS-19617"]
[540,"VK25",53,2.21,0.605,0.85,0.01,88,0.92,5,"04 COL 349/1",42426,"NPS-7614"]
[953,"VTK 1140",183,1.99,0.642,0.885,0.001,61,0.89,5,"06COL513/1OEM09/1",43080,"NPS-34115"]
[952,"VTK 570",183,1,0.642,0.885,0.001,61,0.89,5,"06COL513/1OEM09/1",43080,"NPS-34015"]
[213,"WOLF CFK-1",45,2.12,0.767,3.669,0.018,76,0.952,9,"21208671",41972,"NPS-52711"]
[214,"WOLF CRK-12",45,1.99,0.642,0.885,0.001,61,0.89,5,"06COL513/1OEM06/1",42109,"NPS-35011"]
[356,"WTS-F1",175,2.32,0.802,3.601,0.014,72,0.96,3,"30.0097.0-1",41323,"NPS-4211"]
[354,"WTS-F2 K3",175,2.33,0.814,3.527,0.012,156,0.94,5,"09COL847OEM01",41180,"NPS-25110"]
[355,"WTS-F2 K4",175,2.33,0.814,3.527,0.012,156,0.94,5,"09COL847OEM01",41180,"NPS-25210"]
[848,"WUNDER ALS 2108",159,1.89,0.81,4.335,0.006,72,0.958,15,"12COL1113",42692,"NPS-28714"]
[849,"WUNDER ALS 2510",159,2.23,0.816,4.096,0.01,72,0.957,15,"12COL1114",42690,"NPS-28814"]
[541,"Zelios CF 2",77,1.82,0.7385,4.0045,0.0122,82.76,0.94,25,"1712-3/06/08/pv sottoposto a prova c/o LAMI",41165,"GPS-8252"]
[543,"Zelios XP 2.5 H",77,2.259,0.791,2.717,0.032,91.53,0.95,9,"21211914_SOLATRON S2,5H",41392,"GPS-8460"]
[542,"Zelios XP 2.5 V",77,2.259,0.791,3.104,0.022,84.06,0.926,9,"21211914a_S2,5V",41392,"GPS-8463"]

{"sheet":"Compactos","index":15,"n_rows":347,"n_cols":17,"rows_kept":347,"hidden":true,"flags":["formulas_cached_only"]}
["TS_Codigo","TS_Modelo","TS_Fabricante","TS_Area","TS_Volumen","TS_Inclinacion","TS_Laboratorio","TS_Ensayo","TS_c1","TS_c2","TS_c3","TS_c4","TS_c5","TS_Fecha","TS_Homologacion","TS_EfMaxima","TS_EfMinima"]
[29,"Helio Block 200",24,1.77,178,45,9,"21207326_S200",-1.10336e-06,2.01603e-06,-0.185552729,0.02970954,0.421668194,41442,"SST-2911",2.026563532,0.689256455]
[217,"TA250UFM",62,3.84,250,40,3,"30.1754.0",2.31037e-08,2.87126e-07,-0.043779514,0.002802646,0.201671266,41776,"SST-8212",6.043194633,0.498475113]
[343,"150 TSPRO (QR-D)",50,1.87,150,45,3,"30.1534.6 R",4.14834437630526e-07,7.624000649224966e-07,-0.11022248152069804,0.008989746546175669,0.34038330773777054,43791,"SST-17117",4.707240957692308,0.24274699492385787]
[50,"ALTER-KT-160",90,2.14,155,46,3,"30.1295.0",-1.85215e-06,3.20624e-06,-0.120488435,0.009272648,0.308677611,41784,"SST-1210",5.399876542,0.668250892]
[145,"Astersa AS 150HPE",3,1.8,150,45,3,"30.1696.0",-2.09027e-06,3.70069e-06,-0.183603411,0.018084539,0.421488461,41594,"SST-13211",4.531034077,0.701001559]
[121,"Ecotech F 220",107,2.23,220,40,9,"21214190",-2.05486e-06,3.68885e-06,-0.170357892,0.014267932,0.357532492,41420,"NPS-0911",2.55324106,0.578923501]
[175,"DPE 150 ABL 300",105,2.76,150,49,5,"11SYS87",-1.70046e-06,2.62475e-06,-0.180960302,0.020935473,0.418916544,41710,"SST-2812",3.179533117,1.08067759]
[367,"CORDIVARI STRATOS DR 150",188,0.98,150,45,22,"EN 12976-2",-2.353586935811903e-06,7.125507989447186e-06,-0.7170673327220941,0.23580523205463208,0.758884916294142,44573,"SST 22719",1.1220521250820028,0.4488443362831859]
[136,"SWS 5S/W BE-SSP 300",39,4.72,283,45,8,"IET/400/2017",1.36968e-06,-1.90476e-06,-0.315554922,0.044346532,0.848427919,41951,"SST-1913",3.564070775,1.472101597]
[63,"EGLK 300/4,10",94,3.6,290,45,20,"6043 F2",6.13926e-08,5.50224e-07,-0.156131859,0.018034793,0.429891238,41560,"SST-7511",3.422469838,0.468187172]
[178,"DPE 300 ABL 300",105,2.76,300,49,5,"11SYS87",-4.08827e-07,1.4857e-06,-0.200268176,0.025730115,0.461223165,41710,"SST-3412",1.748877891,0.540338795]
[279,"ESCOSOL BR 300 SV",155,3.8,300,41,3,"30.1427.0-3",-1.0167476112788057e-06,1.8341832346142822e-06,-0.14389342188758097,0.010545397700243205,0.36704830357445734,42686,"GPS-8506",2.8137850487908356,0.7399129484480672]
[70,"GLK 160/3,10",94,2.528,145,45,20,"6042 F2",-4.86603e-07,1.27156e-06,-0.098637878,0.00714788,0.329177553,41560,"SST-9411",6.360527691,0.786698038]
[7,"STS 200 2.5",4,2.37,200,41,3,"30.1427.0-4",-1.31979e-06,2.54936e-06,-0.107813256,0.005063892,0.316661618,41892,"GPS-8454",3.729784188,0.615305217]
[384,"Solahart 302 Kf",194,3.72,300,49,5,"08 COL 733, 10/101.104/2005, 04 COL 341, 045Y530",-1.1922936504727365e-06,2.0879182833497788e-06,-0.1796049870762773,0.01689149978486723,0.40377886944944796,43726,"SST-12317",2.3571832448263343,0.7282827235882194]
[81,"TS-300-HS",53,2,300,45,26,"SYS08_01E",4.07639e-06,-4.49172e-06,-0.814690055,0.1037169,1.838320551,42114,"SST-0710",5.339082479,0.650269688]
[261,"TS300SOL",138,4.28,300,40,11,"30.2286.0",-9.598984246503804e-07,1.5966130575687777e-06,-0.15258868460945788,0.012533469284548675,0.41918095783117304,42530,"SST-26714",3.8484436970633693,0.5555920525530008]
[57,"EGLK 160/2,58",94,2.31,149,45,20,"6043 F2",-6.90414e-07,1.67198e-06,-0.124002591,0.009748989,0.376320709,41560,"SST-6811",5.812032819,0.71885778]
[128,"Ecolamb L 280",109,3.78,280,40,9,"21214190",-1.41744e-06,2.23092e-06,-0.168687245,0.018094704,0.359175986,41420,"NPS-1311",7.954805807,0.73601867]
[19,"Helio Set 150",24,2.01,150,45,12,"Renovación",-1.37216e-06,2.04739e-06,-0.203339169,0.028681655,0.499407131,41432,"SST-150",2.301855165,0.96388994]
[269,"ESCOSOL STAR 150 2.0",155,1.727,143,45,29,"12.V2/LES/2013",-2.1041346153442306e-06,3.4216069425703945e-06,-0.06369465375705705,-0.0014576335570508495,0.27638146038155165,42439,"GPS-8541",2.7551288797074953,0.8988293793846522]
[16,"AS 150 HP 18",3,1.8,145,44,3,"30.1218.2",-1.72035e-06,3.47345e-06,-0.112395237,0.006270584,0.281363941,42045,"SST-5211",2.838720145,0.702575004]
[243,"TA300PFX",62,2.39,300,40,3,"30.1788.0 TA",-2.09802e-06,2.95547e-06,-0.090534119,0.005948053,0.28580394,41776,"SST-9612",6.016206358,2.32703996]
[319,"300 TSBTM (PA-E)",50,4.34,300,45,3,"30.1534.1",-1.862162332155366e-07,6.888252303784831e-07,-0.07401429033333859,0.003048057773826533,0.3778411675879906,43791,"SST-19817",10.924826607692307,0.5633807261869215]
[49,"OKSOL 150",154,1.95,150,40,3,"30.1181.0",-1.10414e-06,2.57253e-06,-0.108634798,0.007867055,0.277138314,41922,"SST-3810",4.90862025,0.506263786]
[316,"200 TSBSM (PA-E)",50,2.17,200,45,3,"30.1534.1",-9.705169708720538e-08,1.3245997239164693e-06,-0.11821754168040774,0.007990652072937476,0.385617634908454,43791,"SST-19517",5.462413303846153,0.28169036309346074]
[87,"HUCUSOL TC 10833120",98,2,120,45,2,"S172  & S173",-2.60845e-06,3.84139e-06,-0.16658615,0.015063601,0.429828751,41596,"SST -13511",5.039327815,1.111719217]
[208,"TA150UF",62,1.92,150,40,3,"30.1754.0-1",-5.36527e-07,1.98223e-06,-0.177852913,0.019276861,0.440033883,41776,"SST-7812",3.021597317,0.249237556]
[86,"VITOSOL 222-T",42,1.5,150,45,9,"21215487_EN_SYS",-2.79373e-06,5.18253e-06,-0.195566599,0.016232082,0.429888748,41412,"SST-0711",2.349324678,0.58411564]
[239,"TA200PF",62,2.39,200,40,3,"30.1788.0 TA",-1.2068e-06,1.64539e-06,-0.106971087,0.009262431,0.341423242,41776,"SST-9012",6.016206358,1.692220427]
[13,"TS 150",26,1.9,148,45,7,"12DER-LECS07",-3.57518e-06,4.74243e-06,-0.172883436,0.021201584,0.372267414,41239,"SST-3910",2.975811259,0.73987981]
[304,"150 TSPTM (PA-E)",50,2.17,150,45,3,"30.1534.0",2.5281074276309496e-08,1.0743436417250387e-06,-0.10244852997188238,0.006735327790498462,0.3585459588155948,43791,"SST-16417",5.462413303846153,0.28169036309346074]
[353,"120 TSBTO (QR-D)",50,1.87,120,45,3,"30.1534.7 R",-1.1596704503503303e-06,2.433229617105739e-06,-0.0652751583662712,0.002201136655650067,0.24258686250483222,43791,"SST-20617",4.707240957692308,0.24274699492385787]
[310,"100 TSBTM (PA-K)",50,1.51,100,45,3,"30.1534.1",3.019766744350845e-07,1.1923524461886839e-06,-0.09477421660228923,0.0066023656424482775,0.33355247357078616,43791,"SST-19917",3.8010341423076928,0.19601495312033443]
[334,"150 TSBTOA (QA-E)",50,2.17,150,45,3,"30.1534.3",1.8104268137811924e-07,7.733062484284351e-07,-0.08416878750716755,0.005644072728553354,0.30129438429785876,43791,"SST-21417",5.462413303846153,0.28169036309346074]
[362,"A1/TS 150/FCC",17,1.94,150,40,9,"21216029_BO_EN_Sys",-3.234654925222095e-06,5.1066944712229184e-06,-0.22787320985376286,0.029933149178390933,0.4014417652792341,42883,"SST-5815",2.22169105511811,0.888434985778995]
[82,"KAIROS THERMO 150-1",65,1.73,150,30,21,"147",6.21465e-07,4.06051e-07,-0.134342179,0.010598684,0.45127891,42354,"GPS-8344",4.35901856,0.499038101]
[108,"Soliker TS 150 G",54,2.35,150,45,3,"30.1729.0",-1.53476e-06,2.62892e-06,-0.148069482,0.01243389,0.389815467,41752,"SST-4312",5.915516712,0.732144066]
[34,"STS 150 B",4,1.89,150,41,3,"30.1427.0-1",-2.02408e-06,3.774e-06,-0.149284251,0.010171765,0.369175682,41892,"GPS-8446",2.974384858,0.58883076]
[88,"HUCUSOL TC 10833150",98,2,150,45,2,"S172  & S173",-2.60845e-06,3.84139e-06,-0.16658615,0.015063601,0.429828751,41596,"SST -13611",5.039327815,1.111719217]
[18,"AS 300 HP 18",3,3.6,280,43.8,3,"30.1218.0",-1.43577e-06,2.12363e-06,-0.09619544,0.005898271,0.279299294,42045,"SST-5411",9.083904463,1.124160379]
[83,"KAIROS THERMO 200-1",65,1.73,200,30,21,"143",-1.65183e-06,3.65412e-06,-0.252036595,0.031099143,0.455629493,42354,"GPS-8336",2.724222727,0.53944656]
[352,"120 TSBRO (QR-K)",50,1.52,120,45,3,"30.1534.7 R",7.237109990013772e-07,5.76170211368986e-07,-0.09643971811760454,0.009142224747043503,0.300502832461498,43791,"SST-20717",3.826206553846154,0.19731306539265453]
[204,"DPS/COMPAC HSH320",122,3.98,320,45,3,"30.1747.0",-2.61342e-07,7.23728e-07,-0.135111491,0.008410308,0.492619471,42105,"SST-6013",10.01861979,0.516648684]
[388,"EGO PRIME 110",206,1.09,105,45,21,"15558 REV 0",-1.0722464909765373e-06,4.100637948763359e-06,-0.21192611859698413,0.022947955298318452,0.44202453607037057,44037,"GPS-8628",1.716417787669173,0.6068957505122952]
[64,"EGLK 300/4,60",94,4.048,290,45,20,"6043 F2",-3.73389e-07,9.74366e-07,-0.130132581,0.009785547,0.385374147,41560,"SST-7611",3.632973561,0.526450465]
[140,"SWS 4S/W BE-SSP 400",39,3.7,365,45,8,"IET/400/2013",1.99368e-06,-2.91624e-06,-0.860442061,0.179226895,1.467882331,41951,"SST-1513",2.326490683,0.960488362]
[203,"DPS/COMPAC VSH320S",122,4.64,320,45,3,"30.1747.0",-1.82768e-07,5.19056e-07,-0.115841147,0.006345125,0.480545663,42105,"SST-5913",11.67999895,0.602324094]
[147,"Astersa AS 300HPE",3,3.6,300,45,3,"30.1696.0",-1.12569e-06,1.5946e-06,-0.077697672,0.004317633,0.311662772,41594,"SST-13411",9.062068154,1.649337212]
[301,"120 TSPRM (PA-K)",50,1.51,120,45,3,"30.1534.0",5.605037150757124e-07,1.0149560819338842e-06,-0.1260162190042772,0.01119260074014399,0.3792231911831791,43791,"SST-16117",3.8010341423076928,0.19601495312033443]
[327,"200 TSPTOA (QA-K)",50,3.02,200,45,3,"30.1534.2",-4.383927951382106e-08,7.717313064194103e-07,-0.07762617049428656,0.004090466586659439,0.31220861749759465,43791,"SST-18717",7.6020682846153855,0.39202990624066886]
[253,"TB300UFX",62,2.39,300,40,3,"30.1754.1 TA",-2.09535e-06,2.93623e-06,-0.08920106,0.005835612,0.290702419,41796,"SST-17012",6.016206358,2.32703996]
[159,"Am-Termosol 24T",114,1.85,250,45,27,"GZ11071587-3",1.04735e-06,4.35859e-07,-1.018919121,0.249937652,1.111771833,41773,"SST-7512",2.346574014,0.332794691]
[142,"SWS 7,5S/W BE-SSP 400",39,7.08,365,45,8,"IET/400/2018",8.13245e-07,-1.14546e-06,-0.359967421,0.051942362,0.881362859,41951,"SST-2013",3.561673725,1.378574651]
[194,"ATERRASOLAR ATS 200",119,1.96,200,45,3,"30.1696.0",9.4823e-08,1.0168e-06,-0.097531453,0.007037682,0.33627956,41959,"SST-9613",4.933792662,0.254430005]
[71,"GLK 200/2,30",94,2.018,186,45,20,"6042 F2",1.76855e-07,1.01158e-06,-0.163026372,0.018670444,0.392438538,41560,"SST-9511",3.160624801,0.523886827]
[372,"ELITE 300 AS",179,3.76,320,40,20,"6035-F1",-2.633478266548346e-07,9.73597186621658e-07,-0.17262921917906154,0.015194991055621844,0.47693052052397306,43231,"SST-11916",3.3745011340418234,0.4889954912049778]
[347,"200 TSPTO (QR-K)",50,3.04,200,45,3,"30.1534.6 R",-4.326434436437895e-08,7.616103496220974e-07,-0.07660813337258614,0.004010263666181566,0.31015461343511064,43791,"SST-17317",7.652413107692308,0.39462613078530906]
[315,"200 TSBRM (PA-F)",50,2.58,200,45,3,"30.1534.1",-1.4628644336069133e-07,1.0800047302061115e-06,-0.08641308060384577,0.0046588664318368495,0.3355684774366582,43791,"SST-19417",6.494482176923078,0.3349129662585847]
[325,"200 TSPROA (QA-F)",50,2.58,200,45,3,"30.1534.2",1.480652614579281e-07,6.468824368492766e-07,-0.08346997289017571,0.0051482825170923886,0.31356995278298083,43791,"SST-18517",6.494482176923078,0.3349129662585847]
[174,"Atlantic CSP 2.5H-1",103,2.26,105,45,3,"30.18.35.0",-1.4274e-06,2.36522e-06,-0.101836533,0.007577859,0.317269158,42069,"GPS-8513",5.688965008,1.035417249]
[55,"EGLK 160/2,05",94,1.8,149,45,20,"6043 F2",-3.04277e-07,1.66726e-06,-0.152166793,0.014329842,0.405316634,41560,"SST-6611",4.528856742,0.560148919]
[235,"TA300UFX",62,2.39,300,40,3,"30.1754.0 TA",-1.47435e-06,2.29128e-06,-0.100290496,0.007447134,0.316329091,41776,"SST-8612",6.016206358,1.329694576]
[202,"DPS/COMPAC VSH320",122,3.98,320,45,3,"30.1747.0",-4.28928e-07,9.66468e-07,-0.122693254,0.007050824,0.47220898,42105,"SST-5813",10.01861979,0.516648684]
[349,"300 TSPTO (QR-E)",50,4.34,300,45,3,"30.1534.6 R",-7.467262291214337e-08,5.521851998785063e-07,-0.06772518343002874,0.0028072075593308927,0.34250334893470313,43791,"SST-17517",10.924826607692307,0.5633807261869215]
[169,"Atlantic CSP 2.5V-1",102,2.26,127,45,3,"30.18.35.0",-1.69976e-06,2.73569e-06,-0.072738627,0.003653974,0.253655041,42069,"GPS-8513",5.688965008,1.035417249]
[144,"Astersa AS 120HPE",3,1.8,120,45,3,"30.1696.0",-1.8645e-06,3.37213e-06,-0.155128779,0.014120215,0.393286229,42045,"SST-13111",4.531034077,0.701001559]
[191,"DPE 150 ABL 150",105,1.38,150,49,5,"11SYS87",-1.34892e-06,3.64464e-06,-0.293585031,0.06040554,0.506796006,41710,"SST-2612",1.589766558,0.63566239]
[198,"ATERRASOLAR ATSB 300",119,3.6,300,45,3,"30.1811.1",5.28386e-07,-2.67044e-07,-0.029537441,0.00132316,0.203832175,41959,"SST-9313",9.062068154,0.467320418]
[234,"TA300UFX",62,2.39,300,40,3,"30.1754.0 TA",-1.47435e-06,2.29128e-06,-0.100290496,0.007447134,0.316329091,41776,"SST-8612",6.016206358,1.329694576]
[272,"ESCOSOL STAR 200 2.5",155,2.118,200,45,29,"12.V2/LES/2013",-1.279160884500665e-06,2.664380109067836e-06,-0.1285143567236816,0.013264510448957004,0.3266587798159603,42439,"GPS-8541",1.9179444601867865,0.8293025852472304]
[387,"EGO PRIME 150",206,1.48,140,45,21,"15558 REV 0",-1.3417069442222026e-06,3.616471425234934e-06,-0.27654666840844466,0.04529628508857667,0.4809805154950464,44037,"GPS-8628",1.69526912448042,0.6786329965193545]
[366,"A1/TS 300/FCC",17,3.84,300,40,9,"21216029_BO_EN_Sys",-1.2806900159782248e-06,2.2147796490479613e-06,-0.2141277282534605,0.028995859881489436,0.39661773133802397,42883,"SST-5915",1.931755240584166,0.7477015058001522]
[284,"TS-200-PRO",53,1.92,198,40,4,"stb-2015-01-k2",1.351673927330636e-07,1.294668274997632e-06,-0.09778240116019082,-0.010046343359686283,0.45045410517888906,43149,"SST-2516",2.204573305263158,0.49722795973074396]
[308,"300 TSPRM (PA-D)",50,3.76,300,45,3,"30.1534.0",-9.448488513883455e-08,7.128724988783596e-07,-0.08786739796760124,0.004127318812879393,0.40015504600945817,43061,"SST-16817",9.464826738461538,0.4880902143923559]
[106,"Soliker TS 150",54,2.05,150,45,3,"30.1729.0",-1.23016e-06,2.45685e-06,-0.135447176,0.011613997,0.36667669,41750,"SST-4112",5.160344365,0.638678866]
[228,"TA300UFX",62,2.39,300,40,3,"30.1754.0 TA",-1.47435e-06,2.29128e-06,-0.100290496,0.007447134,0.316329091,41776,"SST-8612",6.016206358,1.329694576]
[391,"EGO PRIME 260",206,2.64,245,45,21,"15558 REV 0",-6.318436679534289e-07,1.8618039653636037e-06,-0.28230644116734566,0.05046750805964523,0.49352203680850776,44037,"GPS-8628",1.662978179018287,0.6860178075313808]
[163,"Greenheiss PB300",76,3.6,300,45,3,"30.1811.1",-1.06834e-06,1.55295e-06,-0.104291357,0.007015697,0.363236951,41962,"SST-22012",13.45706002,1.649337212]
[148,"Astersa AS 150HPEB",3,1.8,150,45,3,"30.1811.1",-2.13803e-06,3.74758e-06,-0.185352246,0.018575939,0.422233115,41962,"SST-20912",4.531034077,0.701001559]
[229,"TA300UF",62,3.84,300,40,3,"30.1754.0 TA",7.18342e-07,-5.62624e-07,-0.021628728,0.001978072,0.181705841,41776,"SST-8512",9.666206031,2.136413043]
[135,"SWS 4S/W BE-SSP 300",39,3.7,283,45,8,"IET/400/2012",1.78296e-06,-2.55447e-06,-0.560325825,0.098517837,1.152403271,41951,"SST-1413",2.742841274,1.153977947]
[385,"Solahart 181 J",194,1.86,180,49,5,"08 COL 733, 10/101.104/2005, 04 COL 341, 045Y530",-2.9351553533440157e-06,4.9148193640956515e-06,-0.21972101193128463,0.025177030026852835,0.3929018175854256,43726,"SST-12417",2.946657360363086,0.7282827235882194]
[378,"ESCOSOL FMAX 200L 2.4",155,2.23,197,45,20,"6082-F1",-2.682678855365339e-06,4.607602811661971e-06,-0.415015721021807,0.08659211691296141,0.5208390942130621,43565,"GPS-8610",1.6528838289920726,0.6955056273764259]
[270,"ESCOSOL STAR 150 2.5",155,2.118,150,45,29,"12.V2/LES/2013",-1.7374687096480753e-06,2.657747451198021e-06,-0.06394141035474714,0.0012991096009697728,0.2750367582666718,42439,"GPS-8541",3.3789015444241315,1.1023280981683228]
[299,"300 FCPTO (QR-E)",50,4.34,300,45,3,"30.1534.5",-3.099683185191514e-08,3.836942614317421e-07,-0.06180853913452049,0.002544668560726549,0.35128194457540973,43791,"SST-15917",10.924826607692307,0.5633807261869215]
[60,"EGLK 200/2,58",94,2.31,186,45,20,"6043 F2",-4.42362e-07,1.55714e-06,-0.156968889,0.014982357,0.40616522,41560,"SST-7111",3.617960005,0.599692057]
[360,"300 TSBTO (QR-E)",50,4.34,300,45,3,"30.1534.7 R",-1.370379628457248e-07,6.207892268704906e-07,-0.06308930895389278,0.0025495122129319263,0.31831092560660496,43791,"SST-20117",10.924826607692307,0.5633807261869215]
[326,"200 TSPSOA (QA-E)",50,2.17,200,45,3,"30.1534.2",3.1818389685191525e-07,7.305784001127234e-07,-0.11237944574853573,0.008466966157419124,0.3511551804483834,43791,"SST-18617",5.462413303846153,0.28169036309346074]
[196,"ATERRASOLAR ATSB 200",119,1.96,200,45,3,"30.1811.1",9.4823e-08,1.0168e-06,-0.097531453,0.007037682,0.33627956,41959,"SST-9113",4.933792662,0.254430005]
[158,"Am-Termosol 20T",114,1.56,200,45,27,"GZ11071587-2",5.97088e-06,-5.33619e-06,-0.824469109,0.183608818,1.158342385,41773,"SST-7412",2.720757438,0.374174327]
[93,"Sime Natural 320 S",104,3.6,320,35,20,"4085DQ1",-5.35696e-07,1.30649e-06,-0.187713024,0.017391079,0.487119641,41466,"SST-4111",3.230905341,0.468187172]
[307,"200 TSPTM (PA-K)",50,3.02,200,45,3,"30.1534.0",-1.8342334700839524e-07,1.0212573283410297e-06,-0.0903153696787779,0.004586878602827301,0.36548062175913937,43791,"SST-16717",7.6020682846153855,0.39202990624066886]
[275,"OKSOL-150",162,1.95,150,0,11,"30.2378.0",-2.805563627030044e-06,4.3438333175124e-06,-0.23177757295399068,0.029446442875895033,0.4388288564783273,43677,"011-7S1479 A",3.0688097745716867,1.0848972485282826]
[66,"GLK 120/1,89",94,1.64,107,45,20,"6042 F2",-1.08595e-08,1.2355e-06,-0.105619201,0.008566979,0.337572293,41560,"SST-9011",4.126291698,0.638633099]
[220,"FUJI-IP",124,1.24,150,45,29,"10.V1/LES/2011",6.00022e-06,-4.70661e-06,-0.438172044,0.128774826,0.817376188,42262,"SST-13113",1.902173174,0.631563072]
[339,"300 TSBTOA (QA-E)",50,4.34,300,45,3,"30.1534.3",-1.3815929100996241e-07,6.217218469053742e-07,-0.06303860155451035,0.002543523533943975,0.31827826130709996,43791,"SST-21917",10.924826607692307,0.5633807261869215]
[311,"120 TSBRM (PA-K)",50,1.51,120,45,3,"30.1534.1",3.365044825548555e-07,1.2765858707096598e-06,-0.11581526106325227,0.009338529992259707,0.36085468041245944,43791,"SST-19017",3.8010341423076928,0.19601495312033443]
[58,"EGLK 160/3,10",94,2.666,149,45,20,"6043 F2",-7.50602e-07,1.5393e-06,-0.109156375,0.007756149,0.360647077,41560,"SST-6911",6.707740041,0.829642788]
[267,"TSM 300 / S",159,4.14,289,43,22,"M.11.SOLT.0105/4203 Rev.1",-1.290477200565254e-06,1.8676692501373023e-06,-0.02409209118435175,-0.0022776437868081345,0.1928601044051682,42688,"SST-21913",6.56862637090909,0.5404848324324324]
[192,"ATERRASOLAR ATS 120",119,1.8,120,45,3,"30.1696.0",-1.47965e-07,1.52888e-06,-0.112133178,0.008473646,0.351923275,41959,"SST-9413",4.531034077,0.233660209]
[252,"TB250UFM",62,3.84,250,40,3,"30.1754.1 TA",-9.45957e-07,1.27844e-06,-0.0415311,0.001728767,0.219373011,41796,"SST-16912",9.666206031,3.738842446]
[286,"150 FCPRM (PA-D)",50,1.87,150,45,3,"30.1534.4",3.778106253533128e-07,4.6138842684641015e-07,-0.10541602869517554,0.008254176451047191,0.4039395471274017,43791,"SST-14617",4.707240957692308,0.24274699492385787]
[141,"SWS 10S/W BE-SSP 500",39,9.44,452,45,8,"IET/400/2020",6.99613e-07,-9.47638e-07,-0.211120022,0.024111799,0.699873134,41951,"SST-2213",4.7488983,1.838099535]
[67,"GLK 120/2,05",94,1.791,107,45,20,"6042 F2",-1.23229e-07,1.23894e-06,-0.099654752,0.007844183,0.324839768,41560,"SST-9111",4.506212458,0.697434074]
[330,"100 TSBTOA (QA-K)",50,1.51,100,45,3,"30.1534.3",7.36595036941047e-07,4.632170092888956e-07,-0.07425112412317865,0.005918294675692392,0.27478534726881276,43791,"SST-21017",3.8010341423076928,0.19601495312033443]
[348,"300 TSPRO (QR-D)",50,3.74,300,45,3,"30.1534.6 R",-5.106618953480839e-08,6.561476774589814e-07,-0.07992553139871972,0.0037541910844883604,0.3556062022295352,43791,"SST-17417",9.414481915384616,0.48549398984771575]
[190,"DPE 150 ABL 200",105,1.86,150,49,5,"11SYS87",-1.43575e-06,2.96685e-06,-0.216688327,0.032042934,0.456478903,41710,"SST-2612",2.14272884,0.728282724]
[232,"TA200UFM",62,3.84,200,40,3,"30.1754.1-1",-1.00841e-06,1.38101e-06,-0.052303162,0.002421856,0.247004612,41776,"SST-7912",9.666206031,2.718881355]
[167,"Atlantic CSP 2.0V-1",101,1.86,102,45,3,"30.18.35.0",-2.10735e-06,3.49191e-06,-0.150346941,0.013593553,0.385499085,42069,"GPS-8513",4.682068546,0.852157559]
[17,"AS 200 HP 18",3,2,192,44.2,3,"30.1218.1",-3.0204e-06,4.89065e-06,-0.144599456,0.012535287,0.260506898,42045,"SST-5311",5.04661359,0.624533544]
[105,"300ABL600",105,6,272,49,5,"11SYS87",-7.48035e-07,1.12726e-06,-0.136855001,0.012921367,0.369902702,41710,"SST-4012",3.801908459,1.174649554]
[233,"TA300UFM",62,4.78,300,40,3,"30.1754.0 TA",-5.50206e-07,6.6215e-07,-0.041086662,0.001818912,0.252081995,41776,"SST-8412",12.03241272,3.384440853]
[111,"Soliker TS 200 T",54,2.35,192,20,3,"30.1729.0",-1.96527e-06,3.39859e-06,-0.17967238,0.017166908,0.406547159,41756,"SST-4712",5.160344365,0.638678866]
[92,"Sime Natural 200 S",104,2.3,200,35,20,"4079DE1",-8.71375e-07,2.10868e-06,-0.20818534,0.022194716,0.497206685,41466,"SST-4011",3.60229784,0.597095987]
[340,"100 TSPTO (QR-K)",50,1.52,100,45,3,"30.1534.6 R",7.877441294513886e-07,4.68128362413298e-07,-0.09046643746149538,0.007939638123987758,0.3034492245454801,43791,"SST-17817",3.826206553846154,0.19731306539265453]
[314,"150 TSBTM (PA-E)",50,2.17,150,45,3,"30.1534.1",-1.4051673698404133e-07,1.2679055499895419e-06,-0.09560140472324624,0.005777354001083526,0.34301459665657014,43791,"SST-19317",5.462413303846153,0.28169036309346074]
[268,"TSM 200",159,2.42,200,40,22,"M1.12.NRG.0597/48731",-4.190062926929206e-06,5.202968020686984e-06,0.02164049894546569,-0.02286879331104087,0.22503845255248506,42690,"SST-21813",3.83963184,0.47390336756756757]
[162,"Greenheiss PB200",76,1.96,200,45,3,"30.1811.1",-2.20205e-06,3.6646e-06,-0.191095515,0.018803395,0.435176713,41962,"SST-21912",4.933792662,0.763312808]
[2,"THSY 300 2H",39,3.758,282,45,2,"S148EN",-1.44641e-06,1.82895e-06,-0.136494323,0.011179583,0.43192596,41928,"NPS-2310",5.603922466,0.92887367]
[78,"GLK 300/4,60",94,4.036,290,45,20,"6042 F2",-1.58703e-07,7.00918e-07,-0.117943098,0.010034627,0.348943619,41560,"SST-10211",3.622203877,0.524889841]
[323,"150 TSPROA (QA-D)",50,1.87,146,45,3,"30.1534.2",4.14834437630526e-07,7.624000649224966e-07,-0.11022248152069804,0.008989746546175669,0.34038330773777054,43791,"SST-18317",4.707240957692308,0.24274699492385787]
[53,"EGLK 120/1,89",94,1.645,107,45,20,"6043 F2",-4.25472e-07,1.8711e-06,-0.126397312,0.010372649,0.373392227,41560,"SST-6411",4.138871856,0.640580151]
[199,"DPS/COMPAC VSH150",122,1.99,140,45,3,"30.1747.0",-8.91172e-07,2.23836e-06,-0.122711692,0.007958878,0.389590993,42105,"SST-5513",5.009309896,0.258324342]
[75,"GLK 250/4,10",94,3.582,245,45,20,"6042 DE2",-1.5516e-07,7.1217e-07,-0.102972883,0.008322326,0.340641954,41560,"SST-9911",4.101215012,0.697465311]
[110,"Soliker TS 200",54,2.05,192,45,3,"30.1729.0",-1.96527e-06,3.39859e-06,-0.17967238,0.017166908,0.406547159,41754,"SST-4512",5.160344365,0.638678866]
[276,"ESCOSOL BR 150 SV",155,1.9,150,41,3,"30.1427.0-1",-2.5386767493070416e-06,4.291149104832135e-06,-0.17064710407002923,0.015267058153889467,0.3805112655597635,42686,"GPS-8506",2.9901223444544636,0.7399460897608169]
[185,"Helioset 2.250",24,4.66,250,45,9,"21211455c-SD",0.00323772,-0.00427045,-186.3908281,56.90404431,421.7032077,42030,"SST-0412",3.45400836,2.134300619]
[139,"SWS 6S/W BE-SSP 500",39,5.55,452,45,8,"IET/400/2014",1.31822e-06,-1.88801e-06,-0.743875936,0.138263955,1.369231954,41951,"SST-1613",2.791989996,1.080662333]
[393,"CORDIVARI STRATOS DR 220",188,1.4,220,45,20,"EN12976-2",-1.1343518364927814e-06,4.479898053496694e-06,-0.8319743345005375,0.33312152714135257,0.7705128482113985,44573,"SST 22919",1.0376849150622875,0.43664030418250954]
[238,"TA200PFX",62,1.92,200,40,3,"30.1788.0 TA",-1.87352e-06,3.06818e-06,-0.119012591,0.010277528,0.291506489,41776,"SST-9112",4.833103015,1.359440678]
[368,"CORDIVARI STRATOS DR 180",188,1.19,180,45,22,"EN 12976-2",-2.5272202960582666e-06,6.717308742907066e-06,-0.8842031859941688,0.33602860549203195,0.794525156670945,44573,"SST 22819",1.0679937099760026,0.463398407380867]
[28,"Helio Block 150",24,1.77,141,45,9,"21207326_S150",-7.85254e-07,1.59547e-06,-0.150971649,0.022956557,0.392823706,41442,"SST-2811",2.026563532,0.689256455]
[31,"VIH S 300T",57,3.54,285,45,12,"Renovación",-5.28523e-07,9.568e-07,-0.140394571,0.019126556,0.365621749,41797,"SST-2011",2.222057065,0.689287326]
[381,"Solahart 302 J",194,3.72,300,49,5,"08 COL 733, 10/101.104/2005, 04 COL 341, 045Y530",-9.132830576523177e-07,1.7661802301935369e-06,-0.13516643677859996,0.008442118874562442,0.3400510938668219,43726,"SST-12017",2.3571832448263343,0.7282827235882194]
[354,"150 TSBRO (QR-D)",50,1.87,150,45,3,"30.1534.7 R",3.1355664245908927e-07,8.5666407891484e-07,-0.09747404619291329,0.007388695507493662,0.31705302418924486,43791,"SST-20017",4.707240957692308,0.24274699492385787]
[120,"Ecotech F 160",107,1.87,160,40,9,"21214190",-2.33082e-06,4.18761e-06,-0.151147091,0.011090058,0.345730754,41420,"NPS-0811",2.928824766,0.583226692]
[214,"DPS/COMPAC V150 ENAMEL",122,1.99,145,45,3,"30.1932.0",-9.75048e-07,2.31793e-06,-0.106112686,0.005131621,0.377822086,42105,"SST-6513",5.009309896,0.258324342]
[244,"TA300PF",62,3.84,300,40,3,"30.1788.0 TA",-7.79675e-07,1.10913e-06,-0.034055776,0.001389133,0.171844345,41776,"SST-9512",9.666206031,3.738842446]
[331,"120 TSBROA (QA-K)",50,1.51,120,45,3,"30.1534.3",8.134348949480616e-07,5.038313260672261e-07,-0.09626842269687975,0.008790270353361466,0.3029450671761583,43791,"SST-21117",3.8010341423076928,0.19601495312033443]
[394,"CORDIVARI STRATOS DR 260",188,1.61,260,45,20,"EN12976-2",-7.929091388486479e-07,3.782120856988689e-06,-0.7897130415046155,0.314601637952886,0.7331519585240946,44573,"SST 23019",1.0124594254143646,0.4179671909709782]
[74,"GLK 200/4,10",94,3.582,186,45,20,"6040 DE2",1.89014e-07,1.30827e-07,-0.070411031,0.004841414,0.335424855,41560,"SST-9811",5.610187332,0.929912098]
[283,"TS-150-PRO",53,1.92,152,40,4,"stb-2015-01-k2",-6.916270077402586e-07,1.983236978350348e-06,-0.10820310927634351,0.0018290996550251813,0.4108626013273613,43149,"SST-2416",3.0243243898916967,0.5992508981262115]
[168,"Atlantic CSP 2.5H-1",101,2.26,105,45,3,"30.18.35.0",-1.42796e-06,2.36592e-06,-0.101856548,0.007580789,0.317264178,42069,"GPS-8513",5.688965008,1.035417249]
[370,"ELITE 200 AB",179,2.37,200,40,20,"6030-F2",-1.8785847756804123e-07,1.2371077759219527e-06,-0.16643700139136336,0.01575056260164631,0.46308907034574576,43252,"SST-12116",3.7119329919234225,0.6152684736653529]
[54,"EGLK 120/2,05",94,1.8,107,45,20,"6043 F2",-5.91216e-07,1.8802e-06,-0.118652245,0.009256027,0.364143875,41560,"SST-6511",4.528856742,0.700938767]
[91,"Sime Natural 160 S",104,1.88,160,35,20,"4077DE1",-4.34153e-07,1.74333e-06,-0.158523325,0.014122408,0.447567773,41466,"SST-3911",4.730139264,0.585044427]
[8,"STS 300",4,3.78,300,41,3,"30.1427.0-3",-9.82079e-07,1.7517e-06,-0.104828503,0.002847093,0.33667984,41892,"GPS-8452",3.398859153,0.490686439]
[359,"300 TSBRO (QR-D)",50,3.74,300,45,3,"30.1534.7 R",-1.1899269063131292e-07,7.271229644447934e-07,-0.07558706507497487,0.00348651840974893,0.33624478962784143,43791,"SST-20217",9.414481915384616,0.48549398984771575]
[357,"200 TSBSO (QR-E)",50,2.17,200,45,3,"30.1534.7 R",2.267205140953342e-07,8.254218459251378e-07,-0.10373797877825097,0.007522610423750542,0.3326633911188867,43791,"SST-20417",5.462413303846153,0.28169036309346074]
[375,"ESCOSOL FMAX 160L 2.0",155,1.86,156,45,20,"6082-F1",-2.3838474198355088e-06,4.4474944020233154e-06,-0.6540599210801608,0.1502545004662989,0.7631625056865409,43565,"GPS-8610",2.12960913535972,0.8518882300884956]
[172,"Atlantic CSP 2.5V-1",103,2.26,127,45,3,"30.18.35.0",-1.4274e-06,2.36522e-06,-0.101836533,0.007577859,0.317269158,42069,"GPS-8513",5.688965008,1.035417249]
[26,"Helio Set 250",24,4.02,250,45,12,"Renovación",1.67347e-06,-2.14213e-06,-0.355057033,0.046475961,0.977958049,41432,"SST-2611",3.607844298,1.841177788]
[126,"Ecolamb L 160",109,1.87,160,40,9,"21214190",-2.33136e-06,4.1882e-06,-0.151124744,0.011083736,0.345704445,41420,"NPS-1111",2.928824766,0.583226692]
[332,"120 TSBTOA (QA-D)",50,1.87,120,45,3,"30.1534.3",2.735779263344725e-07,7.815835507336054e-07,-0.07774524198050764,0.005401744815073603,0.28144036892453983,43791,"SST-21217",4.707240957692308,0.24274699492385787]
[382,"Solahart 151 Kf",194,1.86,150,49,5,"08 COL 733, 10/101.104/2005, 04 COL 341, 045Y530",-3.059667132206842e-06,4.952594130044958e-06,-0.2023205682223033,0.020605632180052114,0.41547117858845684,43726,"SST-12117",2.946657360363086,0.7282827235882194]
[260,"TS200SOL",138,2.14,200,40,3,"30.2286.0",-4.960445918959075e-07,1.848708875709615e-06,-0.11560320775661997,-0.007400020345199544,0.44261550610212547,42530,"SST-26614",1.9242218485316847,0.2777960262765004]
[117,"Soliker TS 300 GT",54,4.76,290,20,3,"30.1729.0",-8.39149e-07,1.19285e-06,-0.068491666,0.003268334,0.295451275,41761,"SST-5212",11.98206789,1.482981172]
[62,"EGLK 200/4,10",94,3.6,186,45,20,"6041 DE2",-7.56953e-07,1.36004e-06,-0.113874636,0.008505184,0.359121956,41560,"SST-7311",5.638379228,0.934585023]
[33,"STS 200 2.0",4,1.89,200,41,3,"30.1427.0-2",-9.80697e-07,1.97357e-06,-0.09319839,0.007418011,0.208011247,41892,"GPS-8445",2.974384858,0.490686439]
[395,"CORDIVARI STRATOS 4S ROTOSHIELD MOD 120",188,0.73,45,45,2,"EN12976:2017",6.369106345689066e-07,4.417818404372137e-06,-0.3297434211719036,0.06715554268141459,0.6041803488108906,44573,"SST 22519",1.1433380101705055,0.40577751438434984]
[68,"GLK 160/2,30",94,2.018,145,45,20,"6042 F2",-1.79872e-07,1.23816e-06,-0.121003916,0.010495957,0.354744855,41560,"SST-9211",5.077351614,0.627989177]
[322,"120 TSPTOA (QA-D)",50,1.87,120,45,3,"30.1534.2",3.3738395301257835e-07,7.636835567503041e-07,-0.09147214710725578,0.006884020127660813,0.31063482013875043,43791,"SST-18217",4.707240957692308,0.24274699492385787]
[247,"TB150UFM",62,2.39,150,40,3,"30.1754.1 TA",-2.16571e-06,2.97549e-06,-0.093154593,0.006107324,0.316044315,41796,"SST-16312",6.016206358,2.32703996]
[226,"TA200UF",62,2.39,200,40,3,"30.1754.0 TA",1.854e-06,-1.45189e-06,-0.05587959,0.008209484,0.292005504,41776,"SST-8012",6.016206358,1.329694576]
[107,"Soliker TS 150 T",54,2.05,150,20,3,"30.1729.0",-1.23016e-06,2.45685e-06,-0.135447176,0.011613997,0.36667669,41751,"SST-4212",5.160344365,0.638678866]
[223,"DPS/COMPAC V200S ENAMEL",122,2.32,190,45,3,"30.1932.0",-9.20617e-07,2.03739e-06,-0.127213086,0.008398173,0.417120786,42135,"SST-6813",5.839999477,0.301162047]
[116,"Soliker TS 300 G",54,4.76,290,45,3,"30.1729.0",-8.39149e-07,1.19285e-06,-0.068491666,0.003268334,0.295451275,41760,"SST-5112",11.98206789,1.482981172]
[32,"VIH S 200T",57,1.77,178,45,12,"Renovación",-1.10336e-06,2.01603e-06,-0.185552729,0.02970954,0.421668194,41797,"SST-2111",2.043268757,0.689256455]
[48,"SOT-150",154,1.95,150,40,3,"30.1181.0",-1.10414e-06,2.57253e-06,-0.108634798,0.007867055,0.277138314,41922,"SST-3210",4.90862025,0.506263786]
[291,"300 FCPRM (PA-D)",50,3.74,300,45,3,"30.1534.4",-5.945863860674305e-08,5.510685129817675e-07,-0.08040242769382366,0.003694736331193219,0.4048686859522842,43791,"SST-15117",9.414481915384616,0.48549398984771575]
[292,"300 FCPTM (PA-E)",50,4.34,300,45,3,"30.1534.4",-7.171427402857995e-08,4.682269610302998e-07,-0.06856937238557419,0.0027764938945039896,0.3874585348437964,43791,"SST-15217",10.924826607692307,0.5633807261869215]
[25,"VIH S 150T",57,1.77,141,45,12,"Renovación",-7.85254e-07,1.59547e-06,-0.150971649,0.022956557,0.392823706,41797,"SST-1911",2.026563532,0.689256455]
[298,"300 FCPRO (QR-D)",50,3.74,300,45,3,"30.1534.5",1.425976857377818e-08,4.0121899236349703e-07,-0.07361095846583718,0.003518125461417075,0.37242457490091196,43791,"SST-15817",9.414481915384616,0.48549398984771575]
[337,"200 TSBTOA (QA-K)",50,3.02,200,45,3,"30.1534.3",-8.787624706494545e-08,7.901307479406979e-07,-0.07007186118715622,0.003577339369573771,0.2882452130990123,43791,"SST-21717",7.6020682846153855,0.39202990624066886]
[278,"ESCOSOL BR 200 2.5 SV",155,2.38,200,45,3,"30.1427.0-4",-9.608719560824103e-07,2.1894307178110473e-06,-0.07701247544122576,-0.003962067579056128,0.2953192663740775,42686,"GPS-8506",2.7237924826229505,0.6179014416243653]
[297,"200 FCPTO (QR-K)",50,3.02,200,45,3,"30.1534.5",-1.3123555080276168e-06,2.2482952751896562e-06,-0.03485178178258956,-0.0006553630714827592,0.19169718752499412,43791,"SST-15717",7.6020682846153855,0.39202990624066886]
[273,"ESCOSOL STAR 300/2 2.0",155,3.454,300,45,29,"12.V2/LES/2013",-9.49358286714497e-07,1.640058683985387e-06,-0.05689885040111926,-0.0036364765756389506,0.2672617445123386,42439,"GPS-8541",2.592783651096774,0.8988293793846522]
[255,"TB300UFM",62,4.78,300,40,3,"30.1754.1 TA",-6.26803e-07,8.40581e-07,-0.02828334,0.000956911,0.186114935,41796,"SST-17212",12.03241272,4.654079919]
[103,"200ABL400",105,4,181,49,5,"11SYS87",-9.30666e-07,1.509e-06,-0.142903639,0.015507024,0.37350711,41710,"SST-3212",2.98169795,1.044101591]
[263,"SOT-150 2.0",154,2,150,40,11,"30.2067.0-2-1 R Anexo 6",-2.5060338688170686e-06,4.0835254387965524e-06,-0.08035383365489936,-0.00229217700719376,0.2631846958620415,42663,"SST-30514",3.147497204688909,0.7788906208008599]
[164,"SWS 7,5S/W BE-SSP 500",39,7.08,452,45,8,"IET/400/2019",1.02024e-06,-1.41527e-06,-0.416099577,0.061660144,1.003219064,41951,"SST-2113",3.561673725,1.378574651]
[161,"Greenheiss PB150",76,1.8,150,45,3,"30.1811.1",-2.13803e-06,3.74758e-06,-0.185352246,0.018575939,0.422233115,41962,"SST-21812",4.531034077,0.701001559]
[365,"F1/TS 300/FCC",17,3.84,300,35,9,"21216029_BO_EN_Sys",-1.2806900159782248e-06,2.2147796490479613e-06,-0.2141277282534605,0.028995859881489436,0.39661773133802397,42883,"SST-5915",1.931755240584166,0.7477015058001522]
[115,"Soliker TS 300 T",54,4.16,290,20,3,"30.1729.0",-9.77597e-07,1.41409e-06,-0.083823489,0.004503722,0.324349857,41759,"SST-5012",10.4717232,1.296050773]
[89,"HUCUSOL TC 10833200",98,2,200,45,2,"S172  & S173",-2.60845e-06,3.84139e-06,-0.16658615,0.015063601,0.429828751,41596,"SST-13711",5.039327815,1.111719217]
[383,"Solahart 181 Kf",194,1.86,180,49,5,"08 COL 733, 10/101.104/2005, 04 COL 341, 045Y530",-6.463460877155796e-06,9.050693165285434e-06,-0.4555003338643871,0.06413326100787763,0.6759990469430182,43726,"SST-12217",2.946657360363086,0.7282827235882194]
[328,"300 TSPROA (QA-D)",50,3.74,300,45,3,"30.1534.2",-5.106618953480839e-08,6.561476774589814e-07,-0.07992553139871972,0.0037541910844883604,0.3556062022295352,43791,"SST-18817",9.414481915384616,0.48549398984771575]
[206,"2.3 Cu",121,2.1,370,17.5,13,"EL003-09",-8.00256e-07,2.01e-06,-0.110192873,0.006772565,0.369183846,42140,"GPS-8075",5.286206423,0.272603577]
[245,"TA300PFM",62,4.78,300,40,3,"30.1788.0 TA",-5.75914e-07,7.97974e-07,-0.024450983,0.000807796,0.154055713,41776,"SST-9412",12.03241272,4.654079919]
[371,"ELITE 160 AB",179,2.37,160,40,20,"6034-F1",-8.155643378922312e-08,9.779392280464233e-07,-0.12603557154894168,0.00913124608788761,0.43717889533431376,43252,"SST-12216",5.962994710235464,0.7375294101646385]
[27,"Helio Set 250E",24,4.02,250,45,12,"Renovación",2.0634e-06,-2.66321e-06,-0.178303421,0.016432099,0.768732788,41432,"SST-2711",6.296190138,1.841177788]
[65,"EGLK 250/4,10",94,3.6,245,45,20,"6043 DE2",-4.29159e-07,1.04995e-06,-0.115725578,0.008431519,0.377184354,41560,"SST-7411",4.121824133,0.700970162]
[309,"300 TSPTM (PA-E)",50,4.34,300,45,3,"30.1534.0",-9.566424526651147e-08,5.796161942235853e-07,-0.07665359877364024,0.003230906503488734,0.39352896719684394,43791,"SST-16917",10.924826607692307,0.5633807261869215]
[335,"200 TSBROA (QA-F)",50,2.58,200,45,3,"30.1534.3",6.342653764977654e-08,7.457559247010144e-07,-0.07647507342212301,0.004403144375246726,0.2983444619352791,43791,"SST-21517",6.494482176923078,0.3349129662585847]
[369,"ELITE 300 AB",179,3.76,298,40,20,"6035 - f1",1.20234469254907e-08,6.168705945474398e-07,-0.1464115918591489,0.011732956262899484,0.4555004909021739,43252,"SST-12016",3.3745011340418234,0.4889954912049778]
[125,"Perseo 280",108,3.78,280,40,9,"21214190",-1.4609e-06,2.30823e-06,-0.151069368,0.013251388,0.338457368,41420,"NPS-1611",3.392450608,0.73601867]
[114,"Soliker TS 300",54,4.16,290,45,3,"30.1729.0",-9.78172e-07,1.4159e-06,-0.083765123,0.004497471,0.324012876,41758,"SST-4912",10.4717232,1.296050773]
[3,"THSY 160 H",39,1.879,145,45,2,"S149EN",-2.30737e-06,3.1301e-06,-0.150147522,0.014318915,0.42492617,41928,"NPS-2510",4.734448482,0.860590314]
[79,"SA-HP 160",53,2.34,160,50,2,"S138EN",-1.09063e-06,1.55002e-06,-0.093275455,0.006532612,0.368571407,41928,"SST-1010",5.896013544,0.72981308]
[293,"150 FCPRO (QR-D)",50,1.87,150,45,3,"30.1534.5",5.98679918962368e-07,8.694083003052301e-09,-0.09876918810754395,0.008799342187619456,0.37800720031730295,43791,"SST-15317",4.707240957692308,0.24274699492385787]
[80,"TS-160-HS",53,2.24,160,45,26,"SYS08_02E",2.94632e-06,-3.18517e-06,-0.490211321,0.052636669,1.381380761,42113,"SST-0610",5.979772377,0.728302051]
[149,"Astersa AS 200HPEB",3,1.96,200,45,3,"30.1811.1",-3.16169e-06,4.80961e-06,-0.146108994,0.012242722,0.330575817,42057,"SST-21012",4.933792662,0.763312808]
[251,"TB250UF",62,2.39,250,40,3,"30.1754.1 TA",-2.20966e-06,3.05454e-06,-0.092925717,0.006085966,0.305969263,41796,"SST-16812",6.016206358,2.32703996]
[150,"Astersa AS 300HPEB",3,3.6,300,45,3,"30.1811.1",-1.099e-06,1.59386e-06,-0.086034352,0.004986785,0.329342485,41962,"SST-21112",9.062068154,1.402003117]
[212,"DPS/COMPAC V300 ENAMEL",122,3.98,279,45,3,"30.1932.0",-3.79415e-07,8.92815e-07,-0.116275691,0.006801105,0.445144048,42105,"SST-6313",10.01861979,0.516648684]
[182,"auroSTEP plus 2.350",57,4.66,350,45,9,"21211455a-V",-1.20185e-06,1.84604e-06,-0.157404412,0.013881205,0.38351805,41797,"SST-17712",3.45400836,0.907366932]
[122,"Ecotech F 280",107,3.78,280,40,9,"21214190",-1.46019e-06,2.30728e-06,-0.15100293,0.013237283,0.338469088,41420,"NPS-1011",3.392450608,0.73601867]
[137,"SWS 2,5S/W BE-SSP 200",39,2.36,184,45,8,"IET/400/2016",3.86814e-06,-5.31452e-06,-0.314082545,0.044065082,0.950725795,41951,"SST-1813",3.695165483,1.312164226]
[305,"200 TSPRM (PA-F)",50,2.58,200,45,3,"30.1534.0",-4.325517452811918e-08,9.924183437662027e-07,-0.0979100904430577,0.005742138968287172,0.36443111267499684,43791,"SST-16517",6.494482176923078,0.3349129662585847]
[90,"HUCUSOL TC 10833300",98,2,300,45,2,"S172  & S173",-2.60845e-06,3.84139e-06,-0.16658615,0.015063601,0.429828751,41596,"SST-13811",5.039327815,1.111719217]
[73,"GLK 200/3,10",94,2.528,186,45,20,"6042 F2",-3.09656e-07,1.21422e-06,-0.133584988,0.012475469,0.366300994,41560,"SST-9711",3.959395191,0.656286372]
[59,"EGLK 200/2,30",94,2.024,186,45,20,"6043 F2",-2.06274e-07,1.52859e-06,-0.176431974,0.018790276,0.424283972,41560,"SST-7011",3.170022099,0.525444469]
[14,"TS 200",26,1.9,200,45,7,"11DER-LECS07",-2.0535e-06,3.96662e-06,-0.167749661,0.009828081,0.394993703,41239,"SST-4010",2.990122344,0.493282663]
[109,"Soliker TS 150 GT",54,2.35,150,20,3,"30.1729.0",-1.53476e-06,2.62892e-06,-0.148069482,0.01243389,0.389815467,41753,"SST-4412",5.915516712,0.732144066]
[166,"Atlantic CSP 2.5V-1",101,2.26,127,45,3,"30.18.35.0",-1.4274e-06,2.36522e-06,-0.101836533,0.007577859,0.317269158,42069,"GPS-8513",5.688965008,1.035417249]
[157,"Am-Termosol 16T",114,1.24,165,45,27,"GZ11071587-1",5.51083e-06,-4.00265e-06,-0.595926474,0.110276199,0.868471176,41773,"SST-7312",3.460245357,0.356908681]
[329,"300 TSPTOA (QA-E)",50,4.34,300,45,3,"30.1534.2",-7.467262291214337e-08,5.521851998785063e-07,-0.06772518343002874,0.0028072075593308927,0.34250334893470313,43791,"SST-18917",10.924826607692307,0.5633807261869215]
[104,"300ABL474",105,4.74,272,49,5,"11SYS87",-8.00043e-07,1.31948e-06,-0.159955376,0.017447975,0.399567673,41710,"SST-3812",3.003507683,0.927973148]
[216,"TA200UFX",62,1.92,200,40,3,"30.1754.0",4.13311e-05,-5.45664e-05,-4.008183494,0.939602626,6.30163602,41776,"SST-8112",3.021597317,0.249237556]
[118,"RTS Seletivo 200",23,2.24,200,45,22,"M1.11.SOLT.0105/42043rev2",1.03053e-05,-1.25807e-05,-0.324569185,0.051363395,1.251212826,43070,"SST-20115",3.733716361,0.629666506]
[76,"GLK 300/4,10",94,3.582,290,45,20,"6042 F2",2.27833e-07,3.31406e-07,-0.145054389,0.017962176,0.394154493,41560,"SST-10111",3.405357489,0.465846237]
[250,"TB200UFH",62,2.39,200,40,3,"30.1754.1 TA",-2.22725e-06,3.0691e-06,-0.094296752,0.006191555,0.311723332,41796,"SST-16612",6.016206358,2.32703996]
[294,"150 FCPTO (QR-E)",50,2.17,150,45,3,"30.1534.5",3.24851131236143e-07,2.4989771402325783e-07,-0.08301618733300373,0.0061091081402290465,0.34957221739703875,43791,"SST-15417",5.462413303846153,0.28169036309346074]
[193,"ATERRASOLAR ATS 150",119,1.8,150,45,3,"30.1696.0",1.1243e-07,1.2056e-06,-0.115640996,0.009086159,0.366171077,41959,"SST-9513",4.531034077,0.233660209]
[209,"DPS/COMPAC HSH320S",122,4.64,320,45,3,"30.1747.0",-1.82768e-07,5.19056e-07,-0.115841147,0.006345125,0.480545663,42105,"SST-6113",11.67999895,0.602324094]
[374,"ELITE 160 AS",179,1.88,160,40,20,"6035-F1",-1.4481206847619308e-07,1.5251256610319882e-06,-0.16194877139955102,0.013672894821181862,0.4712472301201892,43231,"SST-11716",4.730139263815473,0.5850444266284895]
[123,"Perseo 160",108,1.87,160,40,9,"21214190",-2.33136e-06,4.1882e-06,-0.151124744,0.011083736,0.345704445,41420,"NPS-1411",2.928824766,0.583226692]
[390,"EGO PRIME 220",206,2.25,210,45,21,"15558 REV 0",-9.158986176181246e-07,2.3669236862204394e-06,-0.2955629058953258,0.054209155550703624,0.4997045375838681,44037,"GPS-8628",1.667471847133758,0.701592346865586]
[289,"200 FCPRM (PA-F)",50,2.58,200,45,3,"30.1534.4",2.7141534949363086e-08,6.762624097964401e-07,-0.10095467054339959,0.006330466606344966,0.40645809747131145,43791,"SST-14917",6.494482176923078,0.3349129662585847]
[321,"120 TSPROA (QA-K)",50,1.51,120,45,3,"30.1534.2",8.942666076362539e-07,4.694482887140984e-07,-0.11301666906134224,0.011046399697971264,0.33103623622068223,43791,"SST-18117",3.8010341423076928,0.19601495312033443]
[153,"HIYASU COMPACT SELECT 200",116,2.23,200,45,5,"11SYS87",2.32362e-07,9.66053e-07,-0.309489404,0.103796259,0.456482581,41755,"GPS-8482",1.413042644,0.582086637]
[69,"GLK 160/2,58",94,2.218,145,45,20,"6042 F2",-3.57429e-07,1.29365e-06,-0.112875229,0.009122133,0.347922733,41560,"SST-9311",5.580557919,0.690227946]
[302,"120 TSPTM (PA-D)",50,1.87,120,45,3,"30.1534.0",1.4743566853436573e-07,1.0824984396101297e-06,-0.10148952121104214,0.007137099792624707,0.34929097929439074,43791,"SST-16217",4.707240957692308,0.24274699492385787]
[211,"DPS/COMPAC 3VSH420",122,5.97,420,45,3,"30.1747.0",-8.30135e-08,2.63367e-07,-0.09274993,0.004121501,0.478065423,42105,"SST-7213",15.02792969,0.774973027]
[152,"HIYASU COMPACT SELECT 120",116,1.38,120,45,5,"11SYS87",-1.48251e-06,2.59208e-06,-0.201085622,0.029922613,0.420341307,41755,"GPS-8482",2.568970598,1.027193573]
[210,"DPS/COMPAC 3VSH320",122,5.97,320,45,3,"30.1747.0",-8.66328e-08,2.71096e-07,-0.086816055,0.003823832,0.451954715,42105,"SST-6213",15.02792969,0.774973027]
[113,"Soliker TS 200 GT",54,2.35,192,20,3,"30.1729.0",-2.05197e-06,3.49058e-06,-0.123059052,0.004816369,0.382902749,41757,"SST-4812",23.07237716,0.638678866]
[100,"120ABL200",105,1.86,109,49,5,"11SYS87",-1.9442e-06,3.3457e-06,-0.168180804,0.018020211,0.413719407,41710,"SST-2312",2.94665736,0.856762352]
[84,"KAIROS THERMO 200-2",65,3.46,207,30,22,"M1.09.SOLT.645/35694-3",3.22533e-06,-3.92681e-06,-0.079677591,0.005201278,0.628177613,42339,"GPS-8345",9.374322188,1.17171647]
[346,"200 TSPSO (QR-E)",50,2.17,200,45,3,"30.1534.6 R",3.1818389685191525e-07,7.305784001127234e-07,-0.11237944574853573,0.008466966157419124,0.3511551804483834,43791,"SST-17217",5.462413303846153,0.28169036309346074]
[277,"ESCOSOL BR 200 2.0 SV",155,1.88,200,45,21,"30.1427.0-2",-1.4025463731065408e-06,3.3269607968304935e-06,-0.12362872472346265,-0.0061785001430994,0.36584504719071154,42686,"GPS-8506",2.1515671711475406,0.4880902143923559]
[101,"150ABL237",105,2.23,136,49,5,"11SYS87",-1.63141e-06,2.83669e-06,-0.201099764,0.026873083,0.439392249,41710,"SST-2712",2.568970598,0.873156169]
[290,"200 FCPTM (PA-K)",50,3.02,200,45,3,"30.1534.4",-8.989145135190402e-08,7.182832991727941e-07,-0.0813727960770583,0.004075696355876404,0.37665250867998906,43791,"SST-15017",7.6020682846153855,0.39202990624066886]
[213,"DPS/COMPAC V120 ENAMEL",122,1.99,120,45,3,"30.1932.0",-1.02153e-06,2.33253e-06,-0.08420526,0.002141524,0.343842325,42105,"SST-6413",5.009309896,0.258324342]
[338,"300 TSBROA (QA-D)",50,3.74,300,45,3,"30.1534.3",-1.1899269063131292e-07,7.271229644447934e-07,-0.07558706507497487,0.00348651840974893,0.33624478962784143,43791,"SST-21817",9.414481915384616,0.48549398984771575]
[180,"Helioset 1.150",24,2.33,150,45,9,"21211455c-SD",-5.87502e-07,1.63847e-06,-0.273250961,0.056183465,0.512291783,42030,"SST-0212",1.72700418,0.604884196]
[160,"Am-Termosol 30T",114,2.31,300,45,27,"GZ11071587-4",3.53475e-06,-2.7229e-06,-1.101672339,0.288852012,1.237241216,41773,"SST-7612",2.302179371,0.277032915]
[262,"TS300SOL-PLUS",138,3.7,300,40,3,"30.2286.0-1",-2.7685429006232515e-07,8.71252170879763e-07,-0.10686626785334237,0.005633585107031728,0.45544241595714574,42530,"SST-27014",9.31379226923077,0.48030154075843534]
[274,"ESCOSOL STAR 300/2 2.5",155,4.24,300,45,29,"12.V2/LES/2013",-7.81877336805179e-07,1.259893248376539e-06,-0.05958479849227889,0.0001844556351129474,0.2689613023358523,42439,"GPS-8541",3.1828033238709676,1.1033690123308992]
[189,"auroSTEP plus 1.150",57,2.33,150,45,9,"21211455a-V",-3.10761e-06,5.29528e-06,-0.289799322,0.012354638,0.479457419,41797,"SST-17312",1.465236311,0.453683466]
[61,"EGLK 200/3,10",94,2.666,186,45,20,"6043 F2",-6.57788e-07,1.58759e-06,-0.142840081,0.012677839,0.390056741,41560,"SST-7211",4.175533062,0.692112131]
[237,"TA150PFM",62,2.39,150,40,3,"30.1788.0 TA",-1.76002e-06,2.61312e-06,-0.095827091,0.006865821,0.288670085,41776,"SST-8712",6.016206358,1.692220427]
[241,"TA250PF",62,2.39,250,40,3,"30.1788.0 TA",-3.88611e-07,1.38379e-06,-0.101625087,0.009060496,0.285388358,41776,"SST-9312",6.016206358,1.692220427]
[324,"150 TSPTOA (QA-E)",50,2.17,150,45,3,"30.1534.2",1.71927295311577e-07,8.221487710393405e-07,-0.09332102728668311,0.006467867526054378,0.3205305244144384,43791,"SST-18417",5.462413303846153,0.28169036309346074]
[30,"Helio Block 300",24,3.54,285,45,9,"21207326_S300",-5.28523e-07,9.56799e-07,-0.140394571,0.019126556,0.365621749,41442,"SST-3011",2.226153022,0.689287326]
[296,"200 FCPRO (QR-F)",50,2.58,200,45,3,"30.1534.5",1.5404853637696562e-07,4.290455707469799e-07,-0.0904268743159551,0.005928114990658232,0.3712690112835524,43791,"SST-15617",6.494482176923078,0.3349129662585847]
[246,"TB150UF",62,1.92,150,40,3,"30.1754.1 TA",-3.79264e-06,5.09424e-06,-0.165511328,0.013698062,0.445932641,41796,"SST-16212",4.833103015,1.869421223]
[56,"EGLK 160/2,30",94,2.024,149,45,20,"6043 F2",-5.63382e-07,1.74885e-06,-0.139539469,0.012039763,0.393583132,41560,"SST-6711",5.092447803,0.62985634]
[124,"Perseo 220",108,2.23,220,40,9,"21214190",-2.05486e-06,3.68885e-06,-0.170357892,0.014267932,0.357532492,41420,"NPS-1511",2.55324106,0.578923501]
[281,"Junkers TSS 150 / FCC-2",169,1.94,150,35,9,"21216029_BO_EN_Sys",-2.6343614743401993e-06,4.444021175029311e-06,-0.1506449572954904,0.010701196907862474,0.3447210647429546,43613,"SST-5815",3.0384599174394253,0.6050587072243345]
[176,"DPE 200 ABL 200",105,1.86,200,49,5,"11SYS87",2.58962e-07,1.34196e-06,-0.244496926,0.058325227,0.481105339,41710,"SST-2912",1.386489547,0.48550724]
[266,"SOLCRAFTE 200",155,2.15,195,45,26,"SYS10_06E",-2.0006154145507876e-06,3.4356138385995225e-06,-0.2726704906642272,0.032407116031180086,0.5541996218338534,43804,"SST-20515",3.3673653724199815,0.8372324166965245]
[345,"200 TSPRO (QR-F)",50,2.58,200,45,3,"30.1534.6 R",1.480652614579281e-07,6.468824368492766e-07,-0.08346997289017571,0.0051482825170923886,0.31356995278298083,43791,"SST-17717",6.494482176923078,0.3349129662585847]
[317,"200 TSBTM (PA-K)",50,3.02,200,45,3,"30.1534.1",-2.922650715638208e-07,1.138885070397421e-06,-0.0859950040971211,0.004196784721128187,0.35038895296638223,43791,"SST-19617",7.6020682846153855,0.39202990624066886]
[138,"SWS 8S/W BE-SSP 500",39,7.4,452,45,8,"IET/400/2015",9.68504e-07,-1.33656e-06,-0.37448154,0.053266677,0.948381152,41951,"SST-1713",3.722653328,1.44088311]
[254,"TB300UF",62,3.84,300,40,3,"30.1754.2-1",-9.72186e-07,1.30409e-06,-0.043782727,0.001841631,0.231440292,41796,"SST-17112",9.666206031,3.738842446]
[151,"HIYASU COMPACT SELECT 150",116,2.23,150,45,5,"11SYS87",-9.82816e-07,1.81061e-06,-0.096253072,0.009256158,0.298622151,41755,"GPS-8482",3.532820384,1.247382005]
[51,"ALTER-KT-200",90,2.14,195,45,3,"30.1295.1",-2.17447e-06,3.74394e-06,-0.117582938,0.009226964,0.233105433,41894,"SST-2710",5.399876542,0.668250892]
[259,"TS150SOL",138,2.14,150,40,3,"30.2286.0",-4.393919558056539e-08,1.2092371147773678e-06,-0.05543671029490474,-0.020539243323385126,0.40501780121208125,42530,"SST-26514",1.9242218485316847,0.2777960262765004]
[36,"STS 300 B",4,3.78,300,41,3,"30.1427.0-3",-9.82079e-07,1.7517e-06,-0.104828503,0.002847093,0.33667984,41892,"GPS-8451",3.398859153,0.490686439]
[358,"200 TSBTO (QR-K)",50,3.02,200,45,3,"30.1534.7 R",-1.0355567506845044e-07,8.232597738836433e-07,-0.06915766418498781,0.003439535735436642,0.285047937547121,43791,"SST-20317",7.6020682846153855,0.39202990624066886]
[171,"Atlantic CSP 2.5H-1",102,2.26,105,45,3,"30.18.35.0",-1.4274e-06,2.36522e-06,-0.101836533,0.007577859,0.317269158,42069,"GPS-8513",5.688965008,1.035417249]
[102,"200ABL237",105,2.23,181,49,5,"11SYS87",-2.69406e-07,1.52658e-06,-0.20178397,0.034355759,0.454247425,41710,"SST-3012",1.662296607,0.582086637]
[236,"TA250UF",62,2.39,250,40,3,"30.1754.0 TA",-1.99611e-06,2.89095e-06,-0.109187036,0.008015516,0.322379347,41776,"SST-8312",6.016206358,1.692220427]
[197,"ATERRASOLAR ATS 300",119,3.6,300,45,3,"30.1696.0",2.81074e-08,3.014e-07,-0.028910249,0.00113577,0.183085538,41959,"SST-9713",9.062068154,0.467320418]
[1,"THSY 200 1H",39,1.879,192,45,2,"S150EN",-2.28246e-06,3.10781e-06,-0.190118082,0.019631165,0.49823034,41928,"NPS-2410",4.734448482,0.731702191]
[376,"ESCOSOL FMAX 160L 2.4",155,2.23,156,45,20,"6082-F1",-3.127375211673744e-06,4.68050752910571e-06,-0.28095377596234694,0.03926449579188118,0.47709895525675666,43565,"GPS-8610",2.5532410601355786,1.0213498672566372]
[389,"EGO PRIME 180",206,1.86,175,45,21,"15558 REV 0",-1.3477214166449307e-06,3.1847658962332487e-06,-0.3387282726071713,0.06801285600483394,0.5173528288189566,44037,"GPS-8628",1.673891814369199,0.7249527595481442]
[5,"STS 150",4,1.89,150,41,3,"30.1427.0-1",-2.02408e-06,3.774e-06,-0.149284251,0.010171765,0.369175682,41892,"GPS-8447",2.974384858,0.58883076]
[380,"ESCOSOL FMAX 300L 2.4/2",155,4.46,286,45,20,"6082-F1",-1.3601890747306916e-06,2.1173446705570615e-06,-0.30127142407898583,0.04844361050547812,0.5004260851194806,43565,"GPS-8610",2.2438688129143847,0.8684241447574685]
[38,"Autocalor 150",4,2.23,150,50,2,"S124EN",-1.20088e-06,1.70671e-06,-0.102704474,0.00754779,0.38675206,41892,"GPS-8353",5.618850514,0.695505627]
[280,"DPS/COMPAC VSH300",122,3.98,291,45,3,"30.2227.0",-2.0491652120795243e-07,7.210000976049689e-07,-0.10684173653675635,0.00564683061797492,0.4587225910545445,43154,"SST-2716",10.01861979230769,0.516648684383398]
[318,"300 TSBRM (PA-D)",50,3.74,300,45,3,"30.1534.1",-2.0903085253325002e-07,8.552354670723796e-07,-0.08688780256421638,0.00401207481296573,0.39201131628722263,43066,"SST-19717",9.414481915384616,0.48549398984771575]
[282,"Junkers TSS 300 / FCC-2",169,3.88,300,35,9,"21216029_BO_EN_Sys",-1.5707805113850684e-06,2.431919819170496e-06,-0.17541969090270199,0.016873756460842864,0.3691983624960767,42883,"SST-5915",3.482197978745286,0.7554900631522372]
[379,"ESCOSOL FMAX 300L 2.0/2",155,3.72,286,45,20,"6082-F1",-1.3966164276519364e-06,2.3799588877392333e-06,-0.33989222762341215,0.06286820777498588,0.514019181494097,43569,"GPS-8610",1.8715677094263476,0.7243358337438975]
[181,"Helioset 1.250",24,2.33,250,45,9,"21211455-P-SD / 21211455-R-SD",-5.09056e-07,1.53394e-06,-0.260282077,0.051255893,0.50989585,42030,"SST-0413",1.72700418,0.604884196]
[350,"100 TSBTO (QR-K)",50,1.52,100,45,3,"30.1534.7 R",7.247498178675455e-07,4.596222959505184e-07,-0.07327545115576323,0.005800527166383433,0.2729398448574245,43791,"SST-20817",3.826206553846154,0.19731306539265453]
[227,"TA250UF",62,2.39,250,40,3,"30.1754.0 TA",5.38329e-07,8.35033e-09,-0.12984586,0.013349361,0.400521571,41776,"SST-8312",5.880828317,1.475847296]
[37,"STS 200 2.0 B",4,1.89,200,41,3,"30.1427.0-2",-9.80697e-07,1.97357e-06,-0.09319839,0.007418011,0.208011247,41892,"GPS-8448",2.974384858,0.490686439]
[264,"SOLCRAFTE 100",155,0.95,90,45,26,"SYS10_08E",1.1823259313934363e-06,1.162536158045084e-06,-0.20407956145092945,0.027923406413475533,0.46499041237478717,43804,"SST-20315",2.3902299471407975,0.6715461951219511]
[119,"RTS Seletivo 300",23,3.84,275,45,22,"M1.11.SOLT.0105/42043",3.50779e-06,-4.28202e-06,-0.16523796,0.016084203,0.855687265,42736,"SST-20215",6.362386625,1.072974316]
[249,"TB200UF",62,2.39,200,40,3,"30.1754.1 TA",-2.22889e-06,3.07186e-06,-0.094223634,0.006180299,0.311472657,41796,"SST-16512",6.016206358,2.32703996]
[373,"ELITE 200 AS",179,2.37,200,40,20,"6035-F1",-5.598390055934959e-07,1.7076160541057757e-06,-0.1813899419420691,0.01718304856002493,0.47656987947937024,43231,"SST-11816",3.7119329919234225,0.6152684736653529]
[287,"150 FCPTM (PA-E)",50,2.17,150,45,3,"30.1534.4",1.454747757868667e-07,6.123675421388693e-07,-0.09020406128774423,0.005889918997569439,0.37645718856434973,43791,"SST-14717",5.462413303846153,0.28169036309346074]
[72,"GLK 200/2,58",94,2.31,186,45,20,"6042 F2",-1.22942e-07,1.12105e-06,-0.139944707,0.014115348,0.367120712,41560,"SST-9611",3.617960005,0.599692057]
[248,"TB200UFX",62,1.92,200,40,3,"30.1754.1 TA",-3.45114e-06,4.75559e-06,-0.146113411,0.011942349,0.388030607,41796,"SST-16512",4.833103015,1.869421223]
[52,"ALTER-KT-300",90,4.28,295,45,3,"30.1295.2",-1.1668e-06,1.70173e-06,-0.071036552,0.003691412,0.226845417,41894,"SST-2610",10.79975308,1.336501784]
[392,"CORDIVARI STRATOS DR 110",188,0.77,110,45,20,"EN12976-2",-2.4727273794640974e-06,8.290270389539115e-06,-0.545342530257178,0.13413292300125726,0.7123628924300727,44573,"SST 22619",1.2059866682620402,0.4280118987341772]
[231,"TA150UFM",62,2.39,150,40,3,"30.1754.0 TA",-2.17284e-06,3.06689e-06,-0.112791003,0.008176358,0.343881749,41776,"SST-7712",6.016206358,1.692220427]
[265,"SOLCRAFTE 150",155,1.6,145,45,26,"SYS10_07E",-1.946117084048563e-06,3.642697769208437e-06,-0.23800816900575264,0.025898062584213462,0.5329112287390303,43804,"SST-20415",4.025650437289765,0.8893753739930955]
[288,"200 FCPSM (PA-E)",50,2.17,200,45,3,"30.1534.4",2.2510541772743722e-07,5.548162470421856e-07,-0.11385242511885067,0.00840272377070484,0.42779881747999804,43791,"SST-14817",5.462413303846153,0.28169036309346074]
[377,"ESCOSOL FMAX 200L 2.0",155,1.86,197,45,20,"6082-F1",-2.892076754571304e-06,5.436808153203447e-06,-0.5053217495688147,0.12928216321006447,0.5347940786171175,43565,"GPS-8610",1.378638530011325,0.5801078326996197]
[300,"100 TSPTM (PA-K)",50,1.51,100,45,3,"30.1534.0",4.845454601054225e-07,1.0089349390540447e-06,-0.10641798650080876,0.008415765910624807,0.35537518040753413,43791,"SST-16017",3.8010341423076928,0.19601495312033443]
[364,"A1/TS 200/FCC",17,1.94,200,40,9,"21216029_BO_EN_Sys",-1.9584853441263025e-06,4.068992516674411e-06,-0.26054496901545604,0.04535803861290626,0.4183789498259002,42882,"SST-0812",1.4381383978479398,0.6050587072243345]
[127,"Ecolamb L 220",109,2.23,220,40,9,"21214190",-2.05486e-06,3.68885e-06,-0.170357892,0.014267932,0.357532492,41420,"NPS-1211",2.55324106,0.578923501]
[306,"200 TSPSM (PA-E)",50,2.17,200,45,3,"30.1534.0",8.686168997522813e-08,1.0973605031730694e-06,-0.12203809589737802,0.008682991140505756,0.3926437437225324,43791,"SST-16617",5.462413303846153,0.28169036309346074]
[230,"TA150PF",62,1.92,150,40,3,"30.1788.0-1",-1.72939e-06,2.83983e-06,-0.11114101,0.009525673,0.296053347,41776,"SST-8812",4.833103015,1.359440678]
[341,"120 TSPRO (QR-K)",50,1.52,120,45,3,"30.1534.6 R",8.825386478841056e-07,4.6329165646511324e-07,-0.11153449927578207,0.010829809854789929,0.3288583662455463,43791,"SST-17917",3.826206553846154,0.19731306539265453]
[146,"Astersa AS 200HPE",3,1.96,200,45,3,"30.1696.0",-2.20205e-06,3.6646e-06,-0.191095515,0.018803395,0.435176713,41594,"SST-13311",4.933792662,0.763312808]
[195,"ATERRASOLAR ATSB 150",119,1.8,150,45,3,"30.1811.1",3.9851e-08,2.88056e-07,-0.028924972,0.001140169,0.183572549,41959,"SST-9713",9.062068154,0.467320418]
[184,"Helioset 3.350",24,6.99,350,45,9,"21211455c-SD",-8.94687e-07,1.26136e-06,-0.12089071,0.009036855,0.339900032,42030,"SST-0712",5.18101254,1.361050397]
[200,"DPS/COMPAC VSH200S",122,2.32,170,45,3,"30.1747.0",-7.5103e-07,1.85307e-06,-0.145304811,0.011141345,0.435871464,42105,"SST-5613",5.839999477,0.301162047]
[170,"Atlantic CSP 2.0V-1",102,1.86,102,45,3,"30.18.35.0",-2.10735e-06,3.49191e-06,-0.150346941,0.013593553,0.385499085,42069,"GPS-8513",4.682068546,0.852157559]
[356,"200 TSBRO (QR-F)",50,2.58,200,45,3,"30.1534.7 R",6.342653764977654e-08,7.457559247010144e-07,-0.07647507342212301,0.004403144375246726,0.2983444619352791,43791,"SST-20917",6.494482176923078,0.3349129662585847]
[186,"Helioset 2.350",24,4.66,350,45,9,"21211455c-SD",-1.20185e-06,1.84604e-06,-0.157404412,0.013881205,0.38351805,42030,"SST-0612",3.45400836,0.907366932]
[363,"F1/TS 200/FCC",17,1.94,200,35,9,"21216029_BO_EN_Sys",-1.9584853441263025e-06,4.068992516674411e-06,-0.26054496901545604,0.04535803861290626,0.4183789498259002,42883,"SST-0812",1.4381383978479398,0.6050587072243345]
[240,"TA200PFM",62,3.84,200,40,3,"30.1788.1-1",-8.61538e-07,1.22704e-06,-0.044800507,0.002039281,0.207875925,41776,"SST-8912",9.666206031,2.718881355]
[173,"Atlantic CSP 2.0V-1",103,1.86,102,45,3,"30.18.35.0",-2.10735e-06,3.49191e-06,-0.150346941,0.013593553,0.385499085,42069,"GPS-8513",4.682068546,0.852157559]
[312,"120 TSBTM (PA-D)",50,1.87,120,45,3,"30.1534.1",-9.960482287803187e-09,1.25301761531699e-06,-0.09327089079502905,0.006037700876172685,0.32955755815403026,43791,"SST-19117",4.707240957692308,0.24274699492385787]
[221,"FUJI-IS",124,1.86,300,45,29,"26.V1/LES/2011",2.24279e-06,1.97413e-07,-0.368567593,0.049275375,0.754368783,41908,"SST-19912",6.946841134,0.566089101]
[386,"Solahart 151 J",194,1.86,150,49,5,"08 COL 733, 10/101.104/2005, 04 COL 341, 045Y530",-2.8275799586612165e-06,4.76008318161412e-06,-0.18402950794341136,0.01724225514472563,0.36403166895894007,43726,"SST-12517",2.946657360363086,0.7282827235882194]
[333,"150 TSBROA (QA-D)",50,1.87,150,45,3,"30.1534.3",3.1355664245908927e-07,8.5666407891484e-07,-0.09747404619291329,0.007388695507493662,0.31705302418924486,43791,"SST-21317",4.707240957692308,0.24274699492385787]
[85,"KAIROS THERMO 300-2",65,3.46,280,40,21,"76c",-1.51866e-06,2.28385e-06,-0.157862292,0.013849638,0.392228668,42322,"GPS-8360",5.448445454,0.898025545]
[361,"F1/TS 150/FCC",17,1.94,150,35,9,"21216029_BO_EN_Sys",-3.234654925222095e-06,5.1066944712229184e-06,-0.22787320985376286,0.029933149178390933,0.4014417652792341,42883,"SST-5815",2.22169105511811,0.888434985778995]
[271,"ESCOSOL STAR 200 2.0",155,1.73,200,45,9,"21209464_E200",-4.5589747390582e-07,1.3364367764466826e-06,-0.32366884927226547,0.0996296110108612,0.5060672989948749,42434,"GPS-8540",1.9970931913929786,0.6736800376209243]
[201,"DPS/COMPAC HSH200S",122,2.32,170,45,3,"30.1747.0",-6.6024e-07,1.73162e-06,-0.147969466,0.01154348,0.444428172,42105,"SST-5713",5.839999477,0.301162047]
[313,"150 TSBRM (PA-D)",50,1.87,150,45,3,"30.1534.1",2.8294696398189502e-08,1.3071840790850825e-06,-0.11154698606268153,0.007949725806653332,0.36367221770222485,43791,"SST-19217",4.707240957692308,0.24274699492385787]
[344,"150 TSPTO (QR-E)",50,2.17,150,45,3,"30.1534.6 R",1.71927295311577e-07,8.221487710393405e-07,-0.09332102728668311,0.006467867526054378,0.3205305244144384,43791,"SST-17617",5.462413303846153,0.28169036309346074]
[336,"200 TSBSOA (QA-E)",50,2.17,200,45,3,"30.1534.3",2.2564842411081823e-07,8.266387436474183e-07,-0.10373704740086258,0.007522017286229005,0.33263698089187216,43791,"SST-21617",5.462413303846153,0.28169036309346074]
[112,"Soliker TS 200 G",54,2.05,192,45,3,"30.1729.0",-2.05197e-06,3.49058e-06,-0.123059052,0.004816369,0.382902749,41755,"SST-4612",23.07237716,0.638678866]
[396,"CORDIVARI STRATOS 4S ROTOSHIELD MOD 180",188,1.09,69,45,2,"EN12976:2017",1.1451900899799972e-07,3.5617411545811604e-06,-0.6909312127857065,0.3198988976179763,0.7238847452804275,44573,"SST 22419",0.9782463393897841,0.42445736474381945]
[222,"DPS/COMPAC H200S ENAMEL",122,2.32,190,45,3,"30.1932.0",-9.20617e-07,2.03739e-06,-0.127213086,0.008398173,0.417120786,42135,"SST-6713",5.839999477,0.301162047]
[342,"120 TSPTO (QR-D)",50,1.87,120,45,3,"30.1534.6 R",3.3738395301257835e-07,7.636835567503041e-07,-0.09147214710725578,0.006884020127660813,0.31063482013875043,43791,"SST-17017",4.707240957692308,0.24274699492385787]
[224,"DPS/COMPAC H300 ENAMEL",122,3.98,279,45,3,"30.1932.0",-3.5726e-07,8.22806e-07,-0.115181345,0.006764199,0.449364773,42135,"SST-6913",10.01861979,0.516648684]
[295,"200 FCPSO (QR-E)",50,2.17,200,45,3,"30.1534.5",4.2948312844563433e-07,1.563667830448452e-07,-0.10940975551794915,0.008948460099706802,0.40554799511743367,43791,"SST-15517",5.462413303846153,0.28169036309346074]
[47,"Heatpack 300",87,3.517,300,45,26,"SYS08-02E",7.92126e-07,-8.67839e-07,-0.25616282,0.018259515,1.01331381,41449,"SST-3211",9.38877654,1.143499247]
[46,"Heatpack 160",87,1.995,160,45,26,"SYS08-01E",3.7156e-06,-4.01597e-06,-0.617693315,0.074457875,1.55063461,41449,"SST-3111",5.325734773,0.648644014]
[285,"TS-300-PRO",53,3.84,282,40,4,"stb-2015-01-k2",-2.1714077277683418e-07,8.390391594643136e-07,-0.06063337615247977,-0.011414557050761193,0.3986702624240773,43149,"SST-2616",2.8462214813137034,0.4986984770724421]
[35,"STS 200 2.5 B",4,2.37,200,41,3,"30.1427.0-4",-1.31979e-06,2.54936e-06,-0.107813256,0.005063892,0.316661618,41892,"GPS-8453",2.863427455,0.615305217]
[320,"100 TSPTOA (QA-K)",50,1.51,100,45,3,"30.1534.2",8.49674272019069e-07,4.3154788631222723e-07,-0.09399578617846831,0.008888371266731627,0.3059803932873255,43791,"SST-18017",3.8010341423076928,0.19601495312033443]
[15,"TS 300",26,3.8,293,45,7,"10DER-LECS07",-9.2556e-07,1.32507e-06,-0.133106796,0.01445129,0.38894669,41239,"SST-4110",3.410400082,0.739912948]
[303,"150 TSPRM (PA-D)",50,1.87,150,45,3,"30.1534.0",2.1620045611359459e-07,1.0794552143110654e-06,-0.11831691349630916,0.009081260256663802,0.3763383250402546,43791,"SST-16317",4.707240957692308,0.24274699492385787]
[77,"GLK 250/4,60",94,4.036,245,45,20,"6042 F2",-4.18455e-07,9.41113e-07,-0.110194718,0.009046156,0.332735491,41560,"SST-10011",4.621022834,0.785865437]
[355,"150 TSBTO (QR-E)",50,2.17,150,45,3,"30.1534.7 R",1.0594536525904034e-07,8.672657541896801e-07,-0.08224305526126931,0.005327592689060556,0.29595440110601706,43791,"SST-20517",5.462413303846153,0.28169036309346074]
[177,"DPE 200 ABL 300",105,2.76,200,49,5,"11SYS87",-7.85332e-07,1.75548e-06,-0.19634647,0.028951435,0.445633826,41710,"SST-3112",2.057371585,0.720430098]

{"sheet":"Laboratorios","index":16,"n_rows":29,"n_cols":2,"rows_kept":29,"hidden":true,"flags":["formulas_cached_only"]}
["LA_Codigo","LA_Nombre"]
[23,"AIT"]
[17,"Arsenal Research"]
[14,"Arsenal research (Solar Keymark)"]
[3,"CENER"]
[11,"CENER (Solar Keymark)"]
[20,"Demokritos"]
[21,"ENEA"]
[22,"EUROFINS"]
[4,"Fraunhofer"]
[16,"Fraunhofer (Solar Keymark)"]
[7,"INETI"]
[6,"INTA"]
[27,"Intertek"]
[24,"ISE"]
[8,"ISFH"]
[10,"ISFH (Solar Keymark)"]
[28,"ISTITUTO GIORDANO"]
[19,"ITC"]
[5,"ITW"]
[15,"ITW (Solar Keymark)"]
[13,"LABSOL"]
[25,"LAMI"]
[29,"LNEG"]
[12,"Ministerio de Industria"]
[18,"SP Sveriges Tekniska (Solar Keymark)"]
[2,"SPF"]
[9,"TÜVRheinland"]
[26,"TZSB-IZES gGmbH"]

{"sheet":"Localidad Usuario","index":17,"n_rows":26,"n_cols":15,"rows_kept":26,"merged":[[1,1,2,14],[4,3,4,14],[5,3,5,5],[14,1,15,14],[17,3,17,14],[18,3,18,5],[19,3,19,5],[19,7,20,14],[20,3,20,5]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":2}
[]
[null,"LOCALIDAD DEFINIDA POR EL USUARIO"]
[]
[]
[null,"Nombre de la localidad",null,"Madrid CHEQ4"]
[null,"Latitud",null,{"v":40.4166666667,"d":"40.42 grados norte"}]
[]
[{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic."]
[null,"Tª. media agua  red [ºC]:",null,{"v":8,"d":"8.00"},{"v":8,"d":"8.00"},{"v":10,"d":"10.00"},{"v":12,"d":"12.00"},{"v":14,"d":"14.00"},{"v":17,"d":"17.00"},{"v":20,"d":"20.00"},{"v":19,"d":"19.00"},{"v":17,"d":"17.00"},{"v":13,"d":"13.00"},{"v":10,"d":"10.00"},{"v":8,"d":"8.00"}]
[null,"Tª. media mensual en horas diurnas  [ºC]:",null,{"v":6.2,"d":"6.20"},{"v":7.4,"d":"7.40"},{"v":9.9,"d":"9.90"},{"v":12.2,"d":"12.20"},{"v":16,"d":"16.00"},{"v":20.7,"d":"20.70"},{"v":24.4,"d":"24.40"},{"v":23.9,"d":"23.90"},{"v":20.5,"d":"20.50"},{"v":14.7,"d":"14.70"},{"v":9.4,"d":"9.40"},{"v":6.4,"d":"6.40"}]
[null,"Rad. horiz. [MJ/m2 día]:",null,{"v":8.183804,"d":"8.18"},{"v":11.716899999999999,"d":"11.72"},{"v":16.76418,"d":"16.76"},{"v":20.7299,"d":"20.73"},{"v":23.79432,"d":"23.79"},{"v":27.904248,"d":"27.90"},{"v":28.985807999999995,"d":"28.99"},{"v":25.2364,"d":"25.24"},{"v":19.720444,"d":"19.72"},{"v":12.834512,"d":"12.83"},{"v":8.760636,"d":"8.76"},{"v":6.7417240000000005,"d":"6.74"}]
[]
[]
[]
[null,"IMPORTAR DESDE PLATAFORMA PvGis"]
[]
[]
[null,"Archivo de datos *.csv",null,"C:\\Users\\Monthlydata_40.420_-3.692_SA_2016_2016 (1).csv"]
[null,"Latitud",null,40.42]
[null,"Base de datos",null,"PVGIS-SARAH",{"$nulls":3},"https://re.jrc.ec.europa.eu/pvg_tools/en/tools.html#MR"]
[null,"Año",null,2016]
[]
[{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic."]
[null,"Rad. horiz. [kWh/m2 mes]:",null,45.57,75.54,117.69,153.36,190.87,231.21,240.78,221.65,160.93,116.31,70.42,61.86]
[null,"Rad. horiz. [kWh/m2 día]:",null,1.47,{"v":2.697857142857143,"d":"2.70"},{"v":3.7964516129032257,"d":"3.80"},{"v":5.112,"d":"5.11"},{"v":6.1570967741935485,"d":"6.16"},{"v":7.707,"d":"7.71"},{"v":7.767096774193549,"d":"7.77"},7.15,{"v":5.364333333333334,"d":"5.36"},{"v":3.7519354838709678,"d":"3.75"},{"v":2.3473333333333333,"d":"2.35"},{"v":1.9954838709677418,"d":"2.00"}]
[null,"Rad. horiz. [MJ/m2 día]:",null,{"v":5.292,"d":"5.29"},{"v":9.712285714285715,"d":"9.71"},{"v":13.667225806451613,"d":"13.67"},{"v":18.403200000000002,"d":"18.40"},{"v":22.165548387096774,"d":"22.17"},{"v":27.7452,"d":"27.75"},{"v":27.961548387096776,"d":"27.96"},{"v":25.740000000000002,"d":"25.74"},{"v":19.311600000000002,"d":"19.31"},{"v":13.506967741935485,"d":"13.51"},{"v":8.4504,"d":"8.45"},{"v":7.18374193548387,"d":"7.18"}]

{"sheet":"Importacion","index":18,"n_rows":21,"n_cols":5,"rows_kept":21,"hidden":true,"flags":["formulas_cached_only"]}
["Latitude (decimal degrees):",40.42]
["Longitude (decimal degrees):",-3.692]
["Radiation database:","PVGIS-SARAH"]
[]
["year",null,"month",null,"H(h)_m"]
[2016,null,"Jan",null,45.57]
[2016,null,"Feb",null,75.54]
[2016,null,"Mar",null,117.69]
[2016,null,"Apr",null,153.36]
[2016,null,"May",null,190.87]
[2016,null,"Jun",null,231.21]
[2016,null,"Jul",null,240.78]
[2016,null,"Aug",null,221.65]
[2016,null,"Sep",null,160.93]
[2016,null,"Oct",null,116.31]
[2016,null,"Nov",null,70.42]
[2016,null,"Dec",null,61.86]
[]
["H(h)_m: Irradiation on horizontal plane (kWh/m2/mo)"]
[]
["PVGIS (c) European Union"," 2001-2021"]

{"sheet":"Posicion solar","index":19,"n_rows":893,"n_cols":75,"rows_kept":893,"hidden":true,"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":341}
[]
[null,"DATOS GENERALES"]
[null,"Localidad","Madrid",null,"radianes",null,"inclinacion",null,40,null,"reflexion",null,0.2]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"},null,"azimut",null,15,null,"cte solar",null,1367]
[null,null,"ENERO ","FEBRERO","MARZO","ABRIL","MAYO","JUNIO","JULIO","AGOSTO","SEPTIEMBRE","OCTUBRE","NOVIEMBRE","DICIEMBRE",null,"fila",2]
[null,"Radiacion horizontal (W/m2 dia)",{"v":2273.278888888889,"d":"2,273"},{"v":3254.6944444444443,"d":"3,255"},{"v":4656.716666666666,"d":"4,657"},{"v":5758.305555555556,"d":"5,758"},{"v":6609.533333333333,"d":"6,610"},{"v":7751.179999999999,"d":"7,751"},{"v":8051.613333333331,"d":"8,052"},{"v":7010.111111111111,"d":"7,010"},{"v":5477.901111111111,"d":"5,478"},{"v":3565.1422222222222,"d":"3,565"},{"v":2433.51,"d":"2,434"},{"v":1872.701111111111,"d":"1,873"}]
[null,"COORDENADA SOLAR"]
[{"$nulls":5},0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,"hora solar"]
[null,"mes","dia","n","declinación",{"v":3.141592653589793,"d":"3.14"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.356194490192345,"d":"2.36"},{"v":2.0943951023931953,"d":"2.09"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.0471975511965976,"d":"1.05"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.2617993877991494,"d":"0.26"},{"v":0,"d":"0.00"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-3.141592653589793,"d":"-3.14"},"ang. Horario"]
[null,"Enero",15,15,{"v":-21.304130448775318,"d":"-21.30"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":6.850287211816901,"d":"6.85"},{"v":15.439303497431496,"d":"15.44"},{"v":22.269893182005426,"d":"22.27"},{"v":26.734006314546214,"d":"26.73"},{"v":28.295869551224683,"d":"28.30"},{"v":26.734006314546214,"d":"26.73"},{"v":22.269893182005426,"d":"22.27"},{"v":15.439303497431496,"d":"15.44"},{"v":6.850287211816901,"d":"6.85"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-61.50481807645997,"d":"-61.50"},{"v":-61.50481807645997,"d":"-61.50"},{"v":-61.50481807645997,"d":"-61.50"},{"v":-61.50481807645997,"d":"-61.50"},{"v":-61.50481807645997,"d":"-61.50"},{"v":-61.50481807645997,"d":"-61.50"},{"v":-61.50481807645997,"d":"-61.50"},{"v":-61.50481807645997,"d":"-61.50"},{"v":-54.355353810959535,"d":"-54.36"},{"v":-43.11385592991155,"d":"-43.11"},{"v":-30.223882575663804,"d":"-30.22"},{"v":-15.66389553628639,"d":"-15.66"},{"v":0,"d":"0.00"},{"v":15.66389553628639,"d":"15.66"},{"v":30.223882575663804,"d":"30.22"},{"v":43.11385592991155,"d":"43.11"},{"v":54.355353810959535,"d":"54.36"},{"v":61.50481807645997,"d":"61.50"},{"v":61.50481807645997,"d":"61.50"},{"v":61.50481807645997,"d":"61.50"},{"v":61.50481807645997,"d":"61.50"},{"v":61.50481807645997,"d":"61.50"},{"v":61.50481807645997,"d":"61.50"},{"v":61.50481807645997,"d":"61.50"},{"v":61.50481807645997,"d":"61.50"},"azimut"]
[]
[null,"Febrero",15,46,{"v":-13.36417980101926,"d":"-13.36"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.4046653318499507,"d":"2.40"},{"v":12.747325381925558,"d":"12.75"},{"v":21.96874102203329,"d":"21.97"},{"v":29.46199194597048,"d":"29.46"},{"v":34.46230621483499,"d":"34.46"},{"v":36.235820198980754,"d":"36.24"},{"v":34.46230621483499,"d":"34.46"},{"v":29.46199194597048,"d":"29.46"},{"v":21.96874102203329,"d":"21.97"},{"v":12.747325381925558,"d":"12.75"},{"v":2.4046653318499507,"d":"2.40"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-72.33104453951728,"d":"-72.33"},{"v":-72.33104453951728,"d":"-72.33"},{"v":-72.33104453951728,"d":"-72.33"},{"v":-72.33104453951728,"d":"-72.33"},{"v":-72.33104453951728,"d":"-72.33"},{"v":-72.33104453951728,"d":"-72.33"},{"v":-72.33104453951728,"d":"-72.33"},{"v":-70.15212207232673,"d":"-70.15"},{"v":-59.75346419498467,"d":"-59.75"},{"v":-47.88702418487795,"d":"-47.89"},{"v":-33.96674802700848,"d":"-33.97"},{"v":-17.782850023338845,"d":"-17.78"},{"v":0,"d":"0.00"},{"v":17.782850023338845,"d":"17.78"},{"v":33.96674802700848,"d":"33.97"},{"v":47.88702418487795,"d":"47.89"},{"v":59.75346419498467,"d":"59.75"},{"v":70.15212207232673,"d":"70.15"},{"v":72.33104453951728,"d":"72.33"},{"v":72.33104453951728,"d":"72.33"},{"v":72.33104453951728,"d":"72.33"},{"v":72.33104453951728,"d":"72.33"},{"v":72.33104453951728,"d":"72.33"},{"v":72.33104453951728,"d":"72.33"},{"v":72.33104453951728,"d":"72.33"},"azimut"]
[]
[null,"Marzo",15,74,{"v":-2.9170511384933095,"d":"-2.92"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.4046653318499507,"d":"2.40"},{"v":12.747325381925558,"d":"12.75"},{"v":21.96874102203329,"d":"21.97"},{"v":29.46199194597048,"d":"29.46"},{"v":34.46230621483499,"d":"34.46"},{"v":36.235820198980754,"d":"36.24"},{"v":34.46230621483499,"d":"34.46"},{"v":29.46199194597048,"d":"29.46"},{"v":21.96874102203329,"d":"21.97"},{"v":12.747325381925558,"d":"12.75"},{"v":2.4046653318499507,"d":"2.40"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-86.16832718197654,"d":"-86.17"},{"v":-86.16832718197654,"d":"-86.17"},{"v":-86.16832718197654,"d":"-86.17"},{"v":-86.16832718197654,"d":"-86.17"},{"v":-86.16832718197654,"d":"-86.17"},{"v":-86.16832718197654,"d":"-86.17"},{"v":-86.16832718197654,"d":"-86.17"},{"v":-84.10970483685622,"d":"-84.11"},{"v":-74.86767666492925,"d":"-74.87"},{"v":-65.4573180012773,"d":"-65.46"},{"v":-56.115808771478385,"d":"-56.12"},{"v":-48.306337228956515,"d":"-48.31"},{"v":0,"d":"0.00"},{"v":48.306337228956515,"d":"48.31"},{"v":56.115808771478385,"d":"56.12"},{"v":65.4573180012773,"d":"65.46"},{"v":74.86767666492925,"d":"74.87"},{"v":84.10970483685622,"d":"84.11"},{"v":86.16832718197654,"d":"86.17"},{"v":86.16832718197654,"d":"86.17"},{"v":86.16832718197654,"d":"86.17"},{"v":86.16832718197654,"d":"86.17"},{"v":86.16832718197654,"d":"86.17"},{"v":86.16832718197654,"d":"86.17"},{"v":86.16832718197654,"d":"86.17"},"azimut"]
[]
[null,"Abril",15,105,{"v":9.316357348877686,"d":"9.32"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":6.022629321185504,"d":"6.02"},{"v":17.422891466165577,"d":"17.42"},{"v":28.729031470083463,"d":"28.73"},{"v":39.51700704283348,"d":"39.52"},{"v":49.089503380854524,"d":"49.09"},{"v":56.18182907005419,"d":"56.18"},{"v":58.916357348877696,"d":"58.92"},{"v":56.18182907005419,"d":"56.18"},{"v":49.089503380854524,"d":"49.09"},{"v":39.51700704283348,"d":"39.52"},{"v":28.729031470083463,"d":"28.73"},{"v":17.422891466165577,"d":"17.42"},{"v":6.022629321185504,"d":"6.02"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-102.27341567671603,"d":"-102.27"},{"v":-102.27341567671603,"d":"-102.27"},{"v":-102.27341567671603,"d":"-102.27"},{"v":-102.27341567671603,"d":"-102.27"},{"v":-102.27341567671603,"d":"-102.27"},{"v":-102.27341567671603,"d":"-102.27"},{"v":-97.12106348963694,"d":"-97.12"},{"v":-87.46195600389912,"d":"-87.46"},{"v":-77.05074329846207,"d":"-77.05"},{"v":-64.75882733830426,"d":"-64.76"},{"v":-48.88825233595394,"d":"-48.89"},{"v":-27.316163049604707,"d":"-27.32"},{"v":0,"d":"0.00"},{"v":27.316163049604707,"d":"27.32"},{"v":48.88825233595394,"d":"48.89"},{"v":64.75882733830426,"d":"64.76"},{"v":77.05074329846207,"d":"77.05"},{"v":87.46195600389912,"d":"87.46"},{"v":97.12106348963694,"d":"97.12"},{"v":102.27341567671603,"d":"102.27"},{"v":102.27341567671603,"d":"102.27"},{"v":102.27341567671603,"d":"102.27"},{"v":102.27341567671603,"d":"102.27"},{"v":102.27341567671603,"d":"102.27"},{"v":102.27341567671603,"d":"102.27"},"azimut"]
[]
[null,"Mayo",15,135,{"v":18.722437769945014,"d":"18.72"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1.2242225248041083,"d":"1.22"},{"v":12.007284963597444,"d":"12.01"},{"v":23.247703307757934,"d":"23.25"},{"v":34.6566048232936,"d":"34.66"},{"v":45.89212400629846,"d":"45.89"},{"v":56.371854203616856,"d":"56.37"},{"v":64.7831233479635,"d":"64.78"},{"v":68.32243776994503,"d":"68.32"},{"v":64.7831233479635,"d":"64.78"},{"v":56.371854203616856,"d":"56.37"},{"v":45.89212400629846,"d":"45.89"},{"v":34.6566048232936,"d":"34.66"},{"v":23.247703307757934,"d":"23.25"},{"v":12.007284963597444,"d":"12.01"},{"v":1.2242225248041083,"d":"1.22"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-114.92895244416044,"d":"-114.93"},{"v":-114.92895244416044,"d":"-114.93"},{"v":-114.92895244416044,"d":"-114.93"},{"v":-114.92895244416044,"d":"-114.93"},{"v":-114.92895244416044,"d":"-114.93"},{"v":-113.79109383258444,"d":"-113.79"},{"v":-104.47214307216281,"d":"-104.47"},{"v":-95.34392460521985,"d":"-95.34"},{"v":-85.64446378916524,"d":"-85.64"},{"v":-74.19249886590626,"d":"-74.19"},{"v":-58.768268622706124,"d":"-58.77"},{"v":-35.123833797953466,"d":"-35.12"},{"v":0,"d":"0.00"},{"v":35.123833797953466,"d":"35.12"},{"v":58.768268622706124,"d":"58.77"},{"v":74.19249886590626,"d":"74.19"},{"v":85.64446378916524,"d":"85.64"},{"v":95.34392460521985,"d":"95.34"},{"v":104.47214307216281,"d":"104.47"},{"v":113.79109383258444,"d":"113.79"},{"v":114.92895244416044,"d":"114.93"},{"v":114.92895244416044,"d":"114.93"},{"v":114.92895244416044,"d":"114.93"},{"v":114.92895244416044,"d":"114.93"},{"v":114.92895244416044,"d":"114.93"},"azimut"]
[]
[null,"Junio",15,166,{"v":23.300731046152357,"d":"23.30"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":4.320939299637766,"d":"4.32"},{"v":14.854690758280586,"d":"14.85"},{"v":25.93771709036291,"d":"25.94"},{"v":37.30678790103932,"d":"37.31"},{"v":48.67178014717589,"d":"48.67"},{"v":59.552193912277794,"d":"59.55"},{"v":68.7431176179693,"d":"68.74"},{"v":72.90073104615236,"d":"72.90"},{"v":68.7431176179693,"d":"68.74"},{"v":59.552193912277794,"d":"59.55"},{"v":48.67178014717589,"d":"48.67"},{"v":37.30678790103932,"d":"37.31"},{"v":25.93771709036291,"d":"25.94"},{"v":14.854690758280586,"d":"14.85"},{"v":4.320939299637766,"d":"4.32"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-121.293265658553,"d":"-121.29"},{"v":-121.293265658553,"d":"-121.29"},{"v":-121.293265658553,"d":"-121.29"},{"v":-121.293265658553,"d":"-121.29"},{"v":-121.293265658553,"d":"-121.29"},{"v":-117.16756924638372,"d":"-117.17"},{"v":-108.15854528763074,"d":"-108.16"},{"v":-99.41893427599742,"d":"-99.42"},{"v":-90.25946099157368,"d":"-90.26"},{"v":-79.5584702053399,"d":"-79.56"},{"v":-64.9856249583234,"d":"-64.99"},{"v":-40.96983576081824,"d":"-40.97"},{"v":0,"d":"0.00"},{"v":40.96983576081824,"d":"40.97"},{"v":64.9856249583234,"d":"64.99"},{"v":79.5584702053399,"d":"79.56"},{"v":90.25946099157368,"d":"90.26"},{"v":99.41893427599742,"d":"99.42"},{"v":108.15854528763074,"d":"108.16"},{"v":117.16756924638372,"d":"117.17"},{"v":121.293265658553,"d":"121.29"},{"v":121.293265658553,"d":"121.29"},{"v":121.293265658553,"d":"121.29"},{"v":121.293265658553,"d":"121.29"},{"v":121.293265658553,"d":"121.29"},"azimut"]
[]
[null,"Julio",15,196,{"v":21.56971519372765,"d":"21.57"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":3.15127792023197,"d":"3.15"},{"v":13.78447428176817,"d":"13.78"},{"v":24.933630465796394,"d":"24.93"},{"v":36.325694585862074,"d":"36.33"},{"v":47.650495339564806,"d":"47.65"},{"v":58.385777728159674,"d":"58.39"},{"v":67.27167060625622,"d":"67.27"},{"v":71.16971519372767,"d":"71.17"},{"v":67.27167060625622,"d":"67.27"},{"v":58.385777728159674,"d":"58.39"},{"v":47.650495339564806,"d":"47.65"},{"v":36.325694585862074,"d":"36.33"},{"v":24.933630465796394,"d":"24.93"},{"v":13.78447428176817,"d":"13.78"},{"v":3.15127792023197,"d":"3.15"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-118.86520050370983,"d":"-118.87"},{"v":-118.86520050370983,"d":"-118.87"},{"v":-118.86520050370983,"d":"-118.87"},{"v":-118.86520050370983,"d":"-118.87"},{"v":-118.86520050370983,"d":"-118.87"},{"v":-115.88877716224718,"d":"-115.89"},{"v":-106.7543593341127,"d":"-106.75"},{"v":-97.85749824475866,"d":"-97.86"},{"v":-88.47795382589024,"d":"-88.48"},{"v":-77.46298307306648,"d":"-77.46"},{"v":-62.503971101998715,"d":"-62.50"},{"v":-38.53375678884689,"d":"-38.53"},{"v":0,"d":"0.00"},{"v":38.53375678884689,"d":"38.53"},{"v":62.503971101998715,"d":"62.50"},{"v":77.46298307306648,"d":"77.46"},{"v":88.47795382589024,"d":"88.48"},{"v":97.85749824475866,"d":"97.86"},{"v":106.7543593341127,"d":"106.75"},{"v":115.88877716224718,"d":"115.89"},{"v":118.86520050370983,"d":"118.87"},{"v":118.86520050370983,"d":"118.87"},{"v":118.86520050370983,"d":"118.87"},{"v":118.86520050370983,"d":"118.87"},{"v":118.86520050370983,"d":"118.87"},"azimut"]
[]
[null,"Agosto",15,227,{"v":13.897537859947219,"d":"13.90"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":8.95562938871912,"d":"8.96"},{"v":20.30395504050182,"d":"20.30"},{"v":31.68792706577074,"d":"31.69"},{"v":42.71836129072516,"d":"42.72"},{"v":52.73798456181845,"d":"52.74"},{"v":60.4268147604259,"d":"60.43"},{"v":63.49753785994724,"d":"63.50"},{"v":60.4268147604259,"d":"60.43"},{"v":52.73798456181845,"d":"52.74"},{"v":42.71836129072516,"d":"42.72"},{"v":31.68792706577074,"d":"31.69"},{"v":20.30395504050182,"d":"20.30"},{"v":8.95562938871912,"d":"8.96"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-108.38473683497982,"d":"-108.38"},{"v":-108.38473683497982,"d":"-108.38"},{"v":-108.38473683497982,"d":"-108.38"},{"v":-108.38473683497982,"d":"-108.38"},{"v":-108.38473683497982,"d":"-108.38"},{"v":-108.38473683497982,"d":"-108.38"},{"v":-100.67095316431656,"d":"-100.67"},{"v":-91.22655693917929,"d":"-91.23"},{"v":-81.09889946681224,"d":"-81.10"},{"v":-69.11094736876878,"d":"-69.11"},{"v":-53.28727022570335,"d":"-53.29"},{"v":-30.60173834907428,"d":"-30.60"},{"v":0,"d":"0.00"},{"v":30.60173834907428,"d":"30.60"},{"v":53.28727022570335,"d":"53.29"},{"v":69.11094736876878,"d":"69.11"},{"v":81.09889946681224,"d":"81.10"},{"v":91.22655693917929,"d":"91.23"},{"v":100.67095316431656,"d":"100.67"},{"v":108.38473683497982,"d":"108.38"},{"v":108.38473683497982,"d":"108.38"},{"v":108.38473683497982,"d":"108.38"},{"v":108.38473683497982,"d":"108.38"},{"v":108.38473683497982,"d":"108.38"},{"v":108.38473683497982,"d":"108.38"},"azimut"]
[]
[null,"Septiembre",15,258,{"v":2.365924040979067,"d":"2.37"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1.5331496724646203,"d":"1.53"},{"v":12.925734981340714,"d":"12.93"},{"v":24.029057024245766,"d":"24.03"},{"v":34.3873756857191,"d":"34.39"},{"v":43.291048458830744,"d":"43.29"},{"v":49.61586924207706,"d":"49.62"},{"v":51.965924040979075,"d":"51.97"},{"v":49.61586924207706,"d":"49.62"},{"v":43.291048458830744,"d":"43.29"},{"v":34.3873756857191,"d":"34.39"},{"v":24.029057024245766,"d":"24.03"},{"v":12.925734981340714,"d":"12.93"},{"v":1.5331496724646203,"d":"1.53"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-93.10740986484059,"d":"-93.11"},{"v":-93.10740986484059,"d":"-93.11"},{"v":-93.10740986484059,"d":"-93.11"},{"v":-93.10740986484059,"d":"-93.11"},{"v":-93.10740986484059,"d":"-93.11"},{"v":-93.10740986484059,"d":"-93.11"},{"v":-91.80217199630195,"d":"-91.80"},{"v":-81.96920002772727,"d":"-81.97"},{"v":-71.33192252518094,"d":"-71.33"},{"v":-58.88386213371451,"d":"-58.88"},{"v":-43.341156658358486,"d":"-43.34"},{"v":-23.523658783315327,"d":"-23.52"},{"v":0,"d":"0.00"},{"v":23.523658783315327,"d":"23.52"},{"v":43.341156658358486,"d":"43.34"},{"v":58.88386213371451,"d":"58.88"},{"v":71.33192252518094,"d":"71.33"},{"v":81.96920002772727,"d":"81.97"},{"v":91.80217199630195,"d":"91.80"},{"v":93.10740986484059,"d":"93.11"},{"v":93.10740986484059,"d":"93.11"},{"v":93.10740986484059,"d":"93.11"},{"v":93.10740986484059,"d":"93.11"},{"v":93.10740986484059,"d":"93.11"},{"v":93.10740986484059,"d":"93.11"},"azimut"]
[]
[null,"Octubre",15,288,{"v":-9.45498573874215,"d":"-9.45"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":5.045947847613282,"d":"5.05"},{"v":15.612384200893993,"d":"15.61"},{"v":25.13199969197869,"d":"25.13"},{"v":32.96206496700853,"d":"32.96"},{"v":38.252492785549656,"d":"38.25"},{"v":40.145014261257856,"d":"40.15"},{"v":38.252492785549656,"d":"38.25"},{"v":32.96206496700853,"d":"32.96"},{"v":25.13199969197869,"d":"25.13"},{"v":15.612384200893993,"d":"15.61"},{"v":5.045947847613282,"d":"5.05"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-77.54271858843946,"d":"-77.54"},{"v":-77.54271858843946,"d":"-77.54"},{"v":-77.54271858843946,"d":"-77.54"},{"v":-77.54271858843946,"d":"-77.54"},{"v":-77.54271858843946,"d":"-77.54"},{"v":-77.54271858843946,"d":"-77.54"},{"v":-77.54271858843946,"d":"-77.54"},{"v":-73.04039812922876,"d":"-73.04"},{"v":-62.49695529174983,"d":"-62.50"},{"v":-50.39311157549573,"d":"-50.39"},{"v":-36.00316066576601,"d":"-36.00"},{"v":-18.9720349341868,"d":"-18.97"},{"v":0,"d":"0.00"},{"v":18.9720349341868,"d":"18.97"},{"v":36.00316066576601,"d":"36.00"},{"v":50.39311157549573,"d":"50.39"},{"v":62.49695529174983,"d":"62.50"},{"v":73.04039812922876,"d":"73.04"},{"v":77.54271858843946,"d":"77.54"},{"v":77.54271858843946,"d":"77.54"},{"v":77.54271858843946,"d":"77.54"},{"v":77.54271858843946,"d":"77.54"},{"v":77.54271858843946,"d":"77.54"},{"v":77.54271858843946,"d":"77.54"},{"v":77.54271858843946,"d":"77.54"},"azimut"]
[]
[null,"Noviembre",15,319,{"v":-19.05115319471757,"d":"-19.05"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":8.531855309040818,"d":"8.53"},{"v":17.303926860192668,"d":"17.30"},{"v":24.320109895680652,"d":"24.32"},{"v":28.93029662798056,"d":"28.93"},{"v":30.548846805282434,"d":"30.55"},{"v":28.93029662798056,"d":"28.93"},{"v":24.320109895680652,"d":"24.32"},{"v":17.303926860192668,"d":"17.30"},{"v":8.531855309040818,"d":"8.53"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-64.61985085686628,"d":"-64.62"},{"v":-64.61985085686628,"d":"-64.62"},{"v":-64.61985085686628,"d":"-64.62"},{"v":-64.61985085686628,"d":"-64.62"},{"v":-64.61985085686628,"d":"-64.62"},{"v":-64.61985085686628,"d":"-64.62"},{"v":-64.61985085686628,"d":"-64.62"},{"v":-64.61985085686628,"d":"-64.62"},{"v":-55.86843455851957,"d":"-55.87"},{"v":-44.43192083050875,"d":"-44.43"},{"v":-31.24095999431361,"d":"-31.24"},{"v":-16.23186629219478,"d":"-16.23"},{"v":0,"d":"0.00"},{"v":16.23186629219478,"d":"16.23"},{"v":31.24095999431361,"d":"31.24"},{"v":44.43192083050875,"d":"44.43"},{"v":55.86843455851957,"d":"55.87"},{"v":64.61985085686628,"d":"64.62"},{"v":64.61985085686628,"d":"64.62"},{"v":64.61985085686628,"d":"64.62"},{"v":64.61985085686628,"d":"64.62"},{"v":64.61985085686628,"d":"64.62"},{"v":64.61985085686628,"d":"64.62"},{"v":64.61985085686628,"d":"64.62"},{"v":64.61985085686628,"d":"64.62"},"azimut"]
[]
[null,"Diciembre",15,349,{"v":-23.317287296364064,"d":"-23.32"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":5.343704663466561,"d":"5.34"},{"v":13.766664151090826,"d":"13.77"},{"v":20.43268844188547,"d":"20.43"},{"v":24.76965267297587,"d":"24.77"},{"v":26.282712703635944,"d":"26.28"},{"v":24.76965267297587,"d":"24.77"},{"v":20.43268844188547,"d":"20.43"},{"v":13.766664151090826,"d":"13.77"},{"v":5.343704663466561,"d":"5.34"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},"altura solar"]
[{"$nulls":5},{"v":-58.683366086001605,"d":"-58.68"},{"v":-58.683366086001605,"d":"-58.68"},{"v":-58.683366086001605,"d":"-58.68"},{"v":-58.683366086001605,"d":"-58.68"},{"v":-58.683366086001605,"d":"-58.68"},{"v":-58.683366086001605,"d":"-58.68"},{"v":-58.683366086001605,"d":"-58.68"},{"v":-58.683366086001605,"d":"-58.68"},{"v":-53.01242361798816,"d":"-53.01"},{"v":-41.9561041801499,"d":"-41.96"},{"v":-29.34007956710987,"d":"-29.34"},{"v":-15.174687490983569,"d":"-15.17"},{"v":0,"d":"0.00"},{"v":15.174687490983569,"d":"15.17"},{"v":29.34007956710987,"d":"29.34"},{"v":41.9561041801499,"d":"41.96"},{"v":53.01242361798816,"d":"53.01"},{"v":58.683366086001605,"d":"58.68"},{"v":58.683366086001605,"d":"58.68"},{"v":58.683366086001605,"d":"58.68"},{"v":58.683366086001605,"d":"58.68"},{"v":58.683366086001605,"d":"58.68"},{"v":58.683366086001605,"d":"58.68"},{"v":58.683366086001605,"d":"58.68"},{"v":58.683366086001605,"d":"58.68"},"azimut"]
[]
[null,"OBSTRUCCION SOLAR"]
[null,"COLUMNA",1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49,50,51,52,53,54,55,56,57,58,59,60,61,62,63,64,65,66,67,68,69,70,71,72,73]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[]
[null,"ARCO","azimut","altura",null,"Perdidas orinetacion",false]
[null,"Az este",-75]
[null,"Az oeste",105]
[null,"altura solar",90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90]
[null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"PATIO","azimut","altura","red az"]
[null,"PATIO F1a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"PATIO F1b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"PATIO F2a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"PATIO F2b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"PATIO Ld1",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"PATIO Ld2",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"PATIO Li1",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"PATIO Li2",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"PATIO max",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"SALIENTE","azimut","altura"]
[null,"Sal 1a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"Sal 1b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"Sal 2a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"Sal 2b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"SALIENTE max",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"EDIFICIOS","azimut","altura"]
[null,"Obs1 fr_a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"Obs1 fr_b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"Obs1 lt_a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"Obs1 lt_b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"Obs2 fr1_a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"Obs2 fr1_b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"Obs2 fr2_a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"Obs2 fr2_b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"Obs3 fr_a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"Obs3 fr_b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"Obs3 lt_a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"Obs3 lt_b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"EDIFICIO max",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"GRUPO1","azimut","altura","Perfil edificio"]
[null,"GR1_1A",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"GR1_1B",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"GR1_2A",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"GR1_2B",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"GR1_3A",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"GR1_3B",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"GR1 max",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"GR1 edificio",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"GR1 alero",90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90]
[]
[null,"GRUPO2","azimut","altura","Perfil edificio"]
[null,"GR2_1A",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"GR2_1B",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"GR2_2A",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"GR2_2B",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"GR2_3A",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"GR2_3B",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"GR2 max",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"GR2 edificio",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"GR2 alero",90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90]
[]
[null,"ALERO","azimut","altura"]
[null,"1a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"1b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"2a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"2b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"3a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"3b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"4a",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col inicio",1]
[null,"4b",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},0,"col fin",1]
[null,"altura solar",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"altura interpolada",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"ALERO",90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90]
[]
[null,"PERFILES ENVOLVENTES OBSTRUCCION SOLAR"]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"INFERIOR",90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90]
[null,"h inferior",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"SUPERIOR",90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90]
[null,"h superior",90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90,90]
[]
[null,"FACTORES SOLARES MENSUALES"]
[]
[null,"Localidad","Madrid",null,"radianes",null,"cte solar"]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"},null,{"v":1367,"d":"1,367"},"W/m2"]
[]
[]
[null,"ENERO"]
[null,"Declinacion dia tipo",{"v":-21.183693564513845,"d":"-21.18"},{"v":-0.36972520043430046,"d":"-0.37"}]
[null,"ocaso",{"v":-70.74163977317477,"d":"-70.74"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"},{"v":0.4684081975618065,"d":"0.468"}]
[null,"c",{"v":-0.4493601114613499,"d":"-0.449"},{"v":-0.444954811091373,"d":"-0.445"},{"v":-0.4318727628039942,"d":"-0.432"},{"v":-0.41051145801658995,"d":"-0.411"},{"v":-0.3815199491657837,"d":"-0.382"},{"v":-0.34577912857759585,"d":"-0.346"},{"v":-0.30437496299987055,"d":"-0.304"},{"v":-0.258565497052168,"d":"-0.259"},{"v":-0.20974262817660147,"d":"-0.210"},{"v":-0.1593898145383911,"d":"-0.159"},{"v":-0.10903700090018068,"d":"-0.109"},{"v":-0.060214132024613926,"d":"-0.060"},{"v":-0.014404666076911654,"d":"-0.014"},{"v":0.02699949950081361,"d":"0.027"},{"v":0.06274032008900148,"d":"0.063"},{"v":0.09173182893980772,"d":"0.092"},{"v":0.11309313372721197,"d":"0.113"},{"v":0.1261751820145906,"d":"0.126"},{"v":0.13058048238456757,"d":"0.131"},{"v":0.12617518201459063,"d":"0.126"},{"v":0.11309313372721194,"d":"0.113"},{"v":0.09173182893980775,"d":"0.092"},{"v":0.06274032008900143,"d":"0.063"},{"v":0.026999499500813554,"d":"0.027"},{"v":-0.014404666076911848,"d":"-0.014"},{"v":-0.06021413202461415,"d":"-0.060"},{"v":-0.10903700090018068,"d":"-0.109"},{"v":-0.1593898145383912,"d":"-0.159"},{"v":-0.20974262817660164,"d":"-0.210"},{"v":-0.25856549705216825,"d":"-0.259"},{"v":-0.30437496299987055,"d":"-0.304"},{"v":-0.34577912857759585,"d":"-0.346"},{"v":-0.3815199491657838,"d":"-0.382"},{"v":-0.41051145801659017,"d":"-0.411"},{"v":-0.4318727628039942,"d":"-0.432"},{"v":-0.444954811091373,"d":"-0.445"},{"v":-0.4493601114613499,"d":"-0.449"},{"v":-0.444954811091373,"d":"-0.445"},{"v":-0.4318727628039942,"d":"-0.432"},{"v":-0.41051145801659017,"d":"-0.411"},{"v":-0.3815199491657838,"d":"-0.382"},{"v":-0.34577912857759585,"d":"-0.346"},{"v":-0.30437496299987055,"d":"-0.304"},{"v":-0.25856549705216825,"d":"-0.259"},{"v":-0.20974262817660164,"d":"-0.210"},{"v":-0.1593898145383912,"d":"-0.159"},{"v":-0.10903700090018068,"d":"-0.109"},{"v":-0.06021413202461415,"d":"-0.060"},{"v":-0.014404666076911848,"d":"-0.014"},{"v":0.026999499500813554,"d":"0.027"},{"v":0.06274032008900143,"d":"0.063"},{"v":0.09173182893980775,"d":"0.092"},{"v":0.11309313372721194,"d":"0.113"},{"v":0.12617518201459063,"d":"0.126"},{"v":0.13058048238456757,"d":"0.131"},{"v":0.1261751820145906,"d":"0.126"},{"v":0.11309313372721197,"d":"0.113"},{"v":0.09173182893980772,"d":"0.092"},{"v":0.06274032008900148,"d":"0.063"},{"v":0.02699949950081361,"d":"0.027"},{"v":-0.014404666076911654,"d":"-0.014"},{"v":-0.060214132024613926,"d":"-0.060"},{"v":-0.10903700090018068,"d":"-0.109"},{"v":-0.1593898145383911,"d":"-0.159"},{"v":-0.20974262817660147,"d":"-0.210"},{"v":-0.258565497052168,"d":"-0.259"},{"v":-0.30437496299987055,"d":"-0.304"},{"v":-0.34577912857759585,"d":"-0.346"},{"v":-0.3815199491657837,"d":"-0.382"},{"v":-0.41051145801658995,"d":"-0.411"},{"v":-0.4318727628039942,"d":"-0.432"},{"v":-0.444954811091373,"d":"-0.445"},{"v":-0.4493601114613499,"d":"-0.449"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-9.259993181519466,"d":"-9.26"},{"v":-3.550501680476545,"d":"-3.55"},{"v":1.7013094261415802,"d":"1.70"},{"v":6.439179146440771,"d":"6.44"},{"v":10.645093773790988,"d":"10.65"},{"v":14.327101749335636,"d":"14.33"},{"v":17.508614637259683,"d":"17.51"},{"v":20.220366046874243,"d":"20.22"},{"v":22.494966925552447,"d":"22.49"},{"v":24.363511267913395,"d":"24.36"},{"v":25.853619132221624,"d":"25.85"},{"v":26.988405443568308,"d":"26.99"},{"v":27.786001418416785,"d":"27.79"},{"v":28.25937723718516,"d":"28.26"},{"v":28.416306435486153,"d":"28.42"},{"v":28.25937723718516,"d":"28.26"},{"v":27.786001418416785,"d":"27.79"},{"v":26.988405443568308,"d":"26.99"},{"v":25.853619132221624,"d":"25.85"},{"v":24.363511267913395,"d":"24.36"},{"v":22.494966925552447,"d":"22.49"},{"v":20.220366046874243,"d":"20.22"},{"v":17.508614637259683,"d":"17.51"},{"v":14.327101749335636,"d":"14.33"},{"v":10.645093773790988,"d":"10.65"},{"v":6.439179146440771,"d":"6.44"},{"v":1.7013094261415802,"d":"1.70"},{"v":-3.550501680476545,"d":"-3.55"},{"v":-9.259993181519466,"d":"-9.26"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0.2,"d":"0.20"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",15.5]
[null,"Declinacion . radianes",{"v":-0.36972520043430046,"d":"-0.370"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.234674532301674,"d":"1.235"}]
[null,"Distancia sol - tierra. Bo",{"v":1.0329996421711944,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":0.38117744269619536,"d":"0.381"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":4112.039205702193,"d":"4,112"}]
[null,"H1",{"v":38791.93911776661,"d":"38,792"}]
[null,"H2",{"v":0.6703432788216421,"d":"0.670"}]
[null,"H3",{"v":-0.2891658361254468,"d":"-0.289"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":2273.278888888889,"d":"2,273"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.5528349257313787,"d":"0.553"}]
[null,"Fraccion difusa diaria promedio",{"v":0.33769934803157636,"d":"0.338"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.5024885497214844,"d":"0.502"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.5720523292419625,"d":"0.572"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-9.259993181519466,"d":"-9.26"},{"v":-3.550501680476545,"d":"-3.55"},{"v":1.7013094261415802,"d":"1.70"},{"v":6.439179146440771,"d":"6.44"},{"v":10.645093773790988,"d":"10.65"},{"v":14.327101749335636,"d":"14.33"},{"v":17.508614637259683,"d":"17.51"},{"v":20.220366046874243,"d":"20.22"},{"v":22.494966925552447,"d":"22.49"},{"v":24.363511267913395,"d":"24.36"},{"v":25.853619132221624,"d":"25.85"},{"v":26.988405443568308,"d":"26.99"},{"v":27.786001418416785,"d":"27.79"},{"v":28.25937723718516,"d":"28.26"},{"v":28.416306435486153,"d":"28.42"},{"v":28.25937723718516,"d":"28.26"},{"v":27.786001418416785,"d":"27.79"},{"v":26.988405443568308,"d":"26.99"},{"v":25.853619132221624,"d":"25.85"},{"v":24.363511267913395,"d":"24.36"},{"v":22.494966925552447,"d":"22.49"},{"v":20.220366046874243,"d":"20.22"},{"v":17.508614637259683,"d":"17.51"},{"v":14.327101749335636,"d":"14.33"},{"v":10.645093773790988,"d":"10.65"},{"v":6.439179146440771,"d":"6.44"},{"v":1.7013094261415802,"d":"1.70"},{"v":-3.550501680476545,"d":"-3.55"},{"v":-9.259993181519466,"d":"-9.26"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":70.74163977317474,"d":"70.74"},{"v":84.07577689643847,"d":"84.08"},{"v":75.9590621898364,"d":"75.96"},{"v":68.18324215145184,"d":"68.18"},{"v":60.80611663192147,"d":"60.81"},{"v":53.844730620784325,"d":"53.84"},{"v":47.28740003151706,"d":"47.29"},{"v":41.104415790856216,"d":"41.10"},{"v":35.25613082645563,"d":"35.26"},{"v":29.698421796600023,"d":"29.70"},{"v":24.386037526991093,"d":"24.39"},{"v":19.274432934462883,"d":"19.27"},{"v":14.320594961482108,"d":"14.32"},{"v":9.483232643660163,"d":"9.48"},{"v":4.722583627082686,"d":"4.72"},{"v":0,"d":"0.00"},{"v":-4.722583627082686,"d":"-4.72"},{"v":-9.483232643660163,"d":"-9.48"},{"v":-14.320594961482108,"d":"-14.32"},{"v":-19.274432934462883,"d":"-19.27"},{"v":-24.386037526991093,"d":"-24.39"},{"v":-29.698421796600023,"d":"-29.70"},{"v":-35.25613082645563,"d":"-35.26"},{"v":-41.104415790856216,"d":"-41.10"},{"v":-47.28740003151706,"d":"-47.29"},{"v":-53.844730620784325,"d":"-53.84"},{"v":-60.80611663192147,"d":"-60.81"},{"v":-68.18324215145184,"d":"-68.18"},{"v":-75.9590621898364,"d":"-75.96"},{"v":-84.07577689643847,"d":"-84.08"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"},{"v":-70.74163977317474,"d":"-70.74"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1.4952976386050545,"d":"1.50"},{"v":5.892993722651277,"d":"5.89"},{"v":-16.06860678733117,"d":"-16.07"},{"v":-5.128989542043774,"d":"-5.13"},{"v":-3.5673948019869846,"d":"-3.57"},{"v":-2.9456414082726905,"d":"-2.95"},{"v":-2.61273134147278,"d":"-2.61"},{"v":-2.4059312748819646,"d":"-2.41"},{"v":-2.2653663075042787,"d":"-2.27"},{"v":-2.1638998082299152,"d":"-2.16"},{"v":-2.0874972846138573,"d":"-2.09"},{"v":-2.028217520056667,"d":"-2.03"},{"v":-1.9812799594471098,"d":"-1.98"},{"v":-1.9436937824642317,"d":"-1.94"},{"v":-1.9135667989782874,"d":"-1.91"},{"v":-1.8897443639119642,"d":"-1.89"},{"v":-1.871628937436631,"d":"-1.87"},{"v":-1.8591183917197873,"d":"-1.86"},{"v":-1.8526501022492141,"d":"-1.85"},{"v":-1.853382892122851,"d":"-1.85"},{"v":-1.8636242247479116,"d":"-1.86"},{"v":-1.8877931015938851,"d":"-1.89"},{"v":-1.9347600884708225,"d":"-1.93"},{"v":-2.0244353376753654,"d":"-2.02"},{"v":-2.211321699576399,"d":"-2.21"},{"v":-2.7139929224274035,"d":"-2.71"},{"v":-6.367171004095796,"d":"-6.37"},{"v":1.0328854445688656,"d":"1.03"},{"v":-0.4224303469872998,"d":"-0.42"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1.4952976386050545,"d":"1.50"},{"v":5.892993722651277,"d":"5.89"},{"v":16.06860678733117,"d":"16.07"},{"v":5.128989542043774,"d":"5.13"},{"v":3.5673948019869846,"d":"3.57"},{"v":2.9456414082726905,"d":"2.95"},{"v":2.61273134147278,"d":"2.61"},{"v":2.4059312748819646,"d":"2.41"},{"v":2.2653663075042787,"d":"2.27"},{"v":2.1638998082299152,"d":"2.16"},{"v":2.0874972846138573,"d":"2.09"},{"v":2.028217520056667,"d":"2.03"},{"v":1.9812799594471098,"d":"1.98"},{"v":1.9436937824642317,"d":"1.94"},{"v":1.9135667989782874,"d":"1.91"},{"v":1.8897443639119642,"d":"1.89"},{"v":1.871628937436631,"d":"1.87"},{"v":1.8591183917197873,"d":"1.86"},{"v":1.8526501022492141,"d":"1.85"},{"v":1.853382892122851,"d":"1.85"},{"v":1.8636242247479116,"d":"1.86"},{"v":1.8877931015938851,"d":"1.89"},{"v":1.9347600884708225,"d":"1.93"},{"v":2.0244353376753654,"d":"2.02"},{"v":2.211321699576399,"d":"2.21"},{"v":2.7139929224274035,"d":"2.71"},{"v":6.367171004095796,"d":"6.37"},{"v":1.0328854445688656,"d":"1.03"},{"v":0.4224303469872998,"d":"0.42"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-70.53980822207726,"d":"-70.54"},{"v":-31.00266200230062,"d":"-31.00"},{"v":16.57368651557144,"d":"16.57"},{"v":68.42197091593987,"d":"68.42"},{"v":121.13268225595516,"d":"121.13"},{"v":172.03231803780952,"d":"172.03"},{"v":219.25255460298038,"d":"219.25"},{"v":261.62371158275005,"d":"261.62"},{"v":298.50432737744694,"d":"298.50"},{"v":329.6125004442054,"d":"329.61"},{"v":354.88695766070725,"d":"354.89"},{"v":374.3837527175076,"d":"374.38"},{"v":388.20458623331217,"d":"388.20"},{"v":396.4498512765595,"d":"396.45"},{"v":399.1899221092457,"d":"399.19"},{"v":396.4498512765595,"d":"396.45"},{"v":388.20458623331217,"d":"388.20"},{"v":374.3837527175076,"d":"374.38"},{"v":354.88695766070725,"d":"354.89"},{"v":329.6125004442054,"d":"329.61"},{"v":298.50432737744694,"d":"298.50"},{"v":261.62371158275005,"d":"261.62"},{"v":219.25255460298038,"d":"219.25"},{"v":172.03231803780952,"d":"172.03"},{"v":121.13268225595516,"d":"121.13"},{"v":68.42197091593987,"d":"68.42"},{"v":16.57368651557144,"d":"16.57"},{"v":-31.00266200230062,"d":"-31.00"},{"v":-70.53980822207726,"d":"-70.54"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-42.42190082111882,"d":"-42.42"},{"v":-16.326138787918733,"d":"-16.33"},{"v":7.826926115877145,"d":"7.83"},{"v":29.565665169550286,"d":"29.57"},{"v":48.69897440689451,"d":"48.70"},{"v":65.23711199499276,"d":"65.24"},{"v":79.31279010733236,"d":"79.31"},{"v":91.11880885602966,"d":"91.12"},{"v":100.86533301169644,"d":"100.87"},{"v":108.75368930011858,"d":"108.75"},{"v":114.96192572111195,"d":"114.96"},{"v":119.63785479414908,"d":"119.64"},{"v":122.89640281512615,"d":"122.90"},{"v":124.81914041993105,"d":"124.82"},{"v":125.45467471382612,"d":"125.45"},{"v":124.81914041993105,"d":"124.82"},{"v":122.89640281512615,"d":"122.90"},{"v":119.63785479414908,"d":"119.64"},{"v":114.96192572111195,"d":"114.96"},{"v":108.75368930011858,"d":"108.75"},{"v":100.86533301169644,"d":"100.87"},{"v":91.11880885602966,"d":"91.12"},{"v":79.31279010733236,"d":"79.31"},{"v":65.23711199499276,"d":"65.24"},{"v":48.69897440689451,"d":"48.70"},{"v":29.565665169550286,"d":"29.57"},{"v":7.826926115877145,"d":"7.83"},{"v":-16.326138787918733,"d":"-16.33"},{"v":-42.42190082111882,"d":"-42.42"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":140.54825352568722,"d":"140.55"},{"v":199.29358581568755,"d":"199.29"},{"v":258.3996328693828,"d":"258.40"},{"v":314.5803811247349,"d":"314.58"},{"v":365.6250086160994,"d":"365.63"},{"v":410.22307799092374,"d":"410.22"},{"v":447.72471888519914,"d":"447.72"},{"v":477.9163390805765,"d":"477.92"},{"v":500.8428526847982,"d":"500.84"},{"v":516.680093330723,"d":"516.68"},{"v":525.6497868837699,"d":"525.65"},{"v":527.9669238183683,"d":"527.97"},{"v":523.8106811259826,"d":"523.81"},{"v":513.312604906714,"d":"513.31"},{"v":496.55847342422226,"d":"496.56"},{"v":473.60278404448746,"d":"473.60"},{"v":444.4971349550372,"d":"444.50"},{"v":409.3359421490422,"d":"409.34"},{"v":368.3248176548286,"d":"368.32"},{"v":321.87797915543916,"d":"321.88"},{"v":270.7498711361861,"d":"270.75"},{"v":216.19998900739998,"d":"216.20"},{"v":160.17422994740514,"d":"160.17"},{"v":105.45573878737657,"d":"105.46"},{"v":55.69211919670686,"d":"55.69"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-37.459481105840645,"d":"-37.46"},{"v":-14.416343341996543,"d":"-14.42"},{"v":6.911349686823819,"d":"6.91"},{"v":26.107139339900296,"d":"26.11"},{"v":43.002276568444685,"d":"43.00"},{"v":57.60581956194369,"d":"57.61"},{"v":70.03495611865807,"d":"70.03"},{"v":80.45993302190574,"d":"80.46"},{"v":89.06633043432585,"d":"89.07"},{"v":96.03192432858113,"d":"96.03"},{"v":101.51393504501323,"d":"101.51"},{"v":105.64288432294107,"d":"105.64"},{"v":108.52025463548253,"d":"108.52"},{"v":110.21807466675331,"d":"110.22"},{"v":110.77926557082579,"d":"110.78"},{"v":110.21807466675331,"d":"110.22"},{"v":108.52025463548253,"d":"108.52"},{"v":105.64288432294107,"d":"105.64"},{"v":101.51393504501323,"d":"101.51"},{"v":96.03192432858113,"d":"96.03"},{"v":89.06633043432585,"d":"89.07"},{"v":80.45993302190574,"d":"80.46"},{"v":70.03495611865807,"d":"70.03"},{"v":57.60581956194369,"d":"57.61"},{"v":43.002276568444685,"d":"43.00"},{"v":26.107139339900296,"d":"26.11"},{"v":6.911349686823819,"d":"6.91"},{"v":-14.416343341996543,"d":"-14.42"},{"v":-37.459481105840645,"d":"-37.46"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-1.6503180114876579,"d":"-1.65"},{"v":-0.7253245053542342,"d":"-0.73"},{"v":0.3877506058322001,"d":"0.39"},{"v":1.6007700308535802,"d":"1.60"},{"v":2.833966413368388,"d":"2.83"},{"v":4.024791676806881,"d":"4.02"},{"v":5.129535350972696,"d":"5.13"},{"v":6.1208321136622175,"d":"6.12"},{"v":6.98367461429855,"d":"6.98"},{"v":7.711467609637019,"d":"7.71"},{"v":8.302777580932243,"d":"8.30"},{"v":8.758915935423133,"d":"8.76"},{"v":9.082262015598127,"d":"9.08"},{"v":9.275164573080584,"d":"9.28"},{"v":9.339270052836037,"d":"9.34"},{"v":9.275164573080584,"d":"9.28"},{"v":9.082262015598127,"d":"9.08"},{"v":8.758915935423133,"d":"8.76"},{"v":8.302777580932243,"d":"8.30"},{"v":7.711467609637019,"d":"7.71"},{"v":6.98367461429855,"d":"6.98"},{"v":6.1208321136622175,"d":"6.12"},{"v":5.129535350972696,"d":"5.13"},{"v":4.024791676806881,"d":"4.02"},{"v":2.833966413368388,"d":"2.83"},{"v":1.6007700308535802,"d":"1.60"},{"v":0.3877506058322001,"d":"0.39"},{"v":-0.7253245053542342,"d":"-0.73"},{"v":-1.6503180114876579,"d":"-1.65"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-39.1097991173283,"d":"-39.11"},{"v":-15.141667847350776,"d":"-15.14"},{"v":147.84735381834324,"d":"147.85"},{"v":227.00149518644142,"d":"227.00"},{"v":304.2358758511959,"d":"304.24"},{"v":376.2109923634855,"d":"376.21"},{"v":440.7895000857302,"d":"440.79"},{"v":496.8038431264917,"d":"496.80"},{"v":543.7747239338236,"d":"543.77"},{"v":581.6597310187947,"d":"581.66"},{"v":610.6595653107437,"d":"610.66"},{"v":631.0818935890873,"d":"631.08"},{"v":643.2523035348505,"d":"643.25"},{"v":647.4601630582022,"d":"647.46"},{"v":643.9292167496444,"d":"643.93"},{"v":632.8058441465479,"d":"632.81"},{"v":614.1609900753028,"d":"614.16"},{"v":588.0045843028516,"d":"588.00"},{"v":554.3138475809827,"d":"554.31"},{"v":513.0793340872603,"d":"513.08"},{"v":464.374822703453,"d":"464.37"},{"v":408.4587442910071,"d":"408.46"},{"v":345.9143626058168,"d":"345.91"},{"v":277.83060024615054,"d":"277.83"},{"v":206.01047292921822,"d":"206.01"},{"v":133.16364815813043,"d":"133.16"},{"v":62.991219489362884,"d":"62.99"},{"v":-15.141667847350776,"d":"-15.14"},{"v":-39.1097991173283,"d":"-39.11"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":140.54825352568722,"d":"140.55"},{"v":199.29358581568755,"d":"199.29"},{"v":258.3996328693828,"d":"258.40"},{"v":314.5803811247349,"d":"314.58"},{"v":365.6250086160994,"d":"365.63"},{"v":410.22307799092374,"d":"410.22"},{"v":447.72471888519914,"d":"447.72"},{"v":477.9163390805765,"d":"477.92"},{"v":500.8428526847982,"d":"500.84"},{"v":516.680093330723,"d":"516.68"},{"v":525.6497868837699,"d":"525.65"},{"v":527.9669238183683,"d":"527.97"},{"v":523.8106811259826,"d":"523.81"},{"v":513.312604906714,"d":"513.31"},{"v":496.55847342422226,"d":"496.56"},{"v":473.60278404448746,"d":"473.60"},{"v":444.4971349550372,"d":"444.50"},{"v":409.3359421490422,"d":"409.34"},{"v":368.3248176548286,"d":"368.32"},{"v":321.87797915543916,"d":"321.88"},{"v":270.7498711361861,"d":"270.75"},{"v":216.19998900739998,"d":"216.20"},{"v":160.17422994740514,"d":"160.17"},{"v":105.45573878737657,"d":"105.46"},{"v":55.69211919670686,"d":"55.69"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-39.1097991173283,"d":"-39.11"},{"v":-15.141667847350776,"d":"-15.14"},{"v":147.84735381834324,"d":"147.85"},{"v":227.00149518644142,"d":"227.00"},{"v":304.2358758511959,"d":"304.24"},{"v":376.2109923634855,"d":"376.21"},{"v":440.7895000857302,"d":"440.79"},{"v":496.8038431264917,"d":"496.80"},{"v":543.7747239338236,"d":"543.77"},{"v":581.6597310187947,"d":"581.66"},{"v":610.6595653107436,"d":"610.66"},{"v":631.0818935890873,"d":"631.08"},{"v":643.2523035348505,"d":"643.25"},{"v":647.4601630582022,"d":"647.46"},{"v":643.9292167496444,"d":"643.93"},{"v":632.8058441465479,"d":"632.81"},{"v":614.160990075303,"d":"614.16"},{"v":588.0045843028516,"d":"588.00"},{"v":554.3138475809826,"d":"554.31"},{"v":513.0793340872603,"d":"513.08"},{"v":464.374822703453,"d":"464.37"},{"v":408.4587442910071,"d":"408.46"},{"v":345.9143626058168,"d":"345.91"},{"v":277.83060024615054,"d":"277.83"},{"v":206.01047292921822,"d":"206.01"},{"v":133.16364815813046,"d":"133.16"},{"v":62.991219489362884,"d":"62.99"},{"v":-15.141667847350776,"d":"-15.14"},{"v":-39.1097991173283,"d":"-39.11"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":9045.043020116778,"d":"9,045"},"W/m2"]
[null,"Total Directa disponible",{"v":9045.043020116778,"d":"9,045"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":10987.31219431356,"d":"10,987"}]
[null,"Total global ",{"v":10987.31219431356,"d":"10,987"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.17677382237322747,"d":"0.177"},{"v":0.33769934803157636,"d":"0.338"}]
[]
[null,"FEBRERO"]
[null,"Declinacion dia tipo",{"v":-13.619766412491638,"d":"-13.62"},{"v":-0.23770976725051524,"d":"-0.24"}]
[null,"ocaso",{"v":-78.09992157561065,"d":"-78.10"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"},{"v":0.30523519774240626,"d":"0.305"}]
[null,"c",{"v":-0.5244909809007722,"d":"-0.524"},{"v":-0.5200856805307953,"d":"-0.520"},{"v":-0.5070036322434165,"d":"-0.507"},{"v":-0.4856423274560122,"d":"-0.486"},{"v":-0.45665081860520595,"d":"-0.457"},{"v":-0.4209099980170181,"d":"-0.421"},{"v":-0.3795058324392928,"d":"-0.380"},{"v":-0.3336963664915903,"d":"-0.334"},{"v":-0.28487349761602376,"d":"-0.285"},{"v":-0.23452068397781337,"d":"-0.235"},{"v":-0.18416787033960294,"d":"-0.184"},{"v":-0.1353450014640362,"d":"-0.135"},{"v":-0.08953553551633392,"d":"-0.090"},{"v":-0.048131369938608656,"d":"-0.048"},{"v":-0.01239054935042079,"d":"-0.012"},{"v":0.016600959500385454,"d":"0.017"},{"v":0.0379622642877897,"d":"0.038"},{"v":0.051044312575168345,"d":"0.051"},{"v":0.055449612945145305,"d":"0.055"},{"v":0.05104431257516835,"d":"0.051"},{"v":0.03796226428778968,"d":"0.038"},{"v":0.01660095950038549,"d":"0.017"},{"v":-0.012390549350420832,"d":"-0.012"},{"v":-0.04813136993860871,"d":"-0.048"},{"v":-0.08953553551633411,"d":"-0.090"},{"v":-0.1353450014640364,"d":"-0.135"},{"v":-0.18416787033960294,"d":"-0.184"},{"v":-0.23452068397781348,"d":"-0.235"},{"v":-0.2848734976160239,"d":"-0.285"},{"v":-0.3336963664915905,"d":"-0.334"},{"v":-0.3795058324392928,"d":"-0.380"},{"v":-0.4209099980170181,"d":"-0.421"},{"v":-0.45665081860520607,"d":"-0.457"},{"v":-0.48564232745601243,"d":"-0.486"},{"v":-0.5070036322434165,"d":"-0.507"},{"v":-0.5200856805307953,"d":"-0.520"},{"v":-0.5244909809007722,"d":"-0.524"},{"v":-0.5200856805307953,"d":"-0.520"},{"v":-0.5070036322434165,"d":"-0.507"},{"v":-0.48564232745601243,"d":"-0.486"},{"v":-0.45665081860520607,"d":"-0.457"},{"v":-0.4209099980170181,"d":"-0.421"},{"v":-0.3795058324392928,"d":"-0.380"},{"v":-0.3336963664915905,"d":"-0.334"},{"v":-0.2848734976160239,"d":"-0.285"},{"v":-0.23452068397781348,"d":"-0.235"},{"v":-0.18416787033960294,"d":"-0.184"},{"v":-0.1353450014640364,"d":"-0.135"},{"v":-0.08953553551633411,"d":"-0.090"},{"v":-0.04813136993860871,"d":"-0.048"},{"v":-0.012390549350420832,"d":"-0.012"},{"v":0.01660095950038549,"d":"0.017"},{"v":0.03796226428778968,"d":"0.038"},{"v":0.05104431257516835,"d":"0.051"},{"v":0.055449612945145305,"d":"0.055"},{"v":0.051044312575168345,"d":"0.051"},{"v":0.0379622642877897,"d":"0.038"},{"v":0.016600959500385454,"d":"0.017"},{"v":-0.01239054935042079,"d":"-0.012"},{"v":-0.048131369938608656,"d":"-0.048"},{"v":-0.08953553551633392,"d":"-0.090"},{"v":-0.1353450014640362,"d":"-0.135"},{"v":-0.18416787033960294,"d":"-0.184"},{"v":-0.23452068397781337,"d":"-0.235"},{"v":-0.28487349761602376,"d":"-0.285"},{"v":-0.3336963664915903,"d":"-0.334"},{"v":-0.3795058324392928,"d":"-0.380"},{"v":-0.4209099980170181,"d":"-0.421"},{"v":-0.45665081860520595,"d":"-0.457"},{"v":-0.4856423274560122,"d":"-0.486"},{"v":-0.5070036322434165,"d":"-0.507"},{"v":-0.5200856805307953,"d":"-0.520"},{"v":-0.5244909809007722,"d":"-0.524"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-3.425803921840662,"d":"-3.43"},{"v":2.192345281558839,"d":"2.19"},{"v":7.417337436093509,"d":"7.42"},{"v":12.178218401014066,"d":"12.18"},{"v":16.443075536746864,"d":"16.44"},{"v":20.2093774658641,"d":"20.21"},{"v":23.49377168512995,"d":"23.49"},{"v":26.32351600237338,"d":"26.32"},{"v":28.730207397019836,"d":"28.73"},{"v":30.745629397199306,"d":"30.75"},{"v":32.3992290703087,"d":"32.40"},{"v":33.71671600287632,"d":"33.72"},{"v":34.71937083277206,"d":"34.72"},{"v":35.423766382422265,"d":"35.42"},{"v":35.841703068173494,"d":"35.84"},{"v":35.980233587508366,"d":"35.98"},{"v":35.841703068173494,"d":"35.84"},{"v":35.423766382422265,"d":"35.42"},{"v":34.71937083277206,"d":"34.72"},{"v":33.71671600287632,"d":"33.72"},{"v":32.3992290703087,"d":"32.40"},{"v":30.745629397199306,"d":"30.75"},{"v":28.730207397019836,"d":"28.73"},{"v":26.32351600237338,"d":"26.32"},{"v":23.49377168512995,"d":"23.49"},{"v":20.2093774658641,"d":"20.21"},{"v":16.443075536746864,"d":"16.44"},{"v":12.178218401014066,"d":"12.18"},{"v":7.417337436093509,"d":"7.42"},{"v":2.192345281558839,"d":"2.19"},{"v":-3.425803921840662,"d":"-3.43"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",45]
[null,"Declinacion . radianes",{"v":-0.23770976725051524,"d":"-0.238"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.3631007770437633,"d":"1.363"}]
[null,"Distancia sol - tierra. Bo",{"v":1.032996984001652,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":0.5161843279657656,"d":"0.516"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":5568.442657677495,"d":"5,568"}]
[null,"H1",{"v":38481.852187435776,"d":"38,482"}]
[null,"H2",{"v":0.724217495577656,"d":"0.724"}]
[null,"H3",{"v":-0.2080331676118904,"d":"-0.208"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":3254.6944444444443,"d":"3,255"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.584489173100675,"d":"0.584"}]
[null,"Fraccion difusa diaria promedio",{"v":0.33894926514481216,"d":"0.339"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.5648346445052124,"d":"0.565"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.5128011661969004,"d":"0.513"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-3.425803921840662,"d":"-3.43"},{"v":2.192345281558839,"d":"2.19"},{"v":7.417337436093509,"d":"7.42"},{"v":12.178218401014066,"d":"12.18"},{"v":16.443075536746864,"d":"16.44"},{"v":20.2093774658641,"d":"20.21"},{"v":23.49377168512995,"d":"23.49"},{"v":26.32351600237338,"d":"26.32"},{"v":28.730207397019836,"d":"28.73"},{"v":30.745629397199306,"d":"30.75"},{"v":32.3992290703087,"d":"32.40"},{"v":33.71671600287632,"d":"33.72"},{"v":34.71937083277206,"d":"34.72"},{"v":35.423766382422265,"d":"35.42"},{"v":35.841703068173494,"d":"35.84"},{"v":35.980233587508366,"d":"35.98"},{"v":35.841703068173494,"d":"35.84"},{"v":35.423766382422265,"d":"35.42"},{"v":34.71937083277206,"d":"34.72"},{"v":33.71671600287632,"d":"33.72"},{"v":32.3992290703087,"d":"32.40"},{"v":30.745629397199306,"d":"30.75"},{"v":28.730207397019836,"d":"28.73"},{"v":26.32351600237338,"d":"26.32"},{"v":23.49377168512995,"d":"23.49"},{"v":20.2093774658641,"d":"20.21"},{"v":16.443075536746864,"d":"16.44"},{"v":12.178218401014066,"d":"12.18"},{"v":7.417337436093509,"d":"7.42"},{"v":2.192345281558839,"d":"2.19"},{"v":-3.425803921840662,"d":"-3.43"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":78.09992157561065,"d":"78.10"},{"v":82.79223117965132,"d":"82.79"},{"v":75.05498875176778,"d":"75.05"},{"v":67.62729030678001,"d":"67.63"},{"v":60.578556843340394,"d":"60.58"},{"v":53.938123153721385,"d":"53.94"},{"v":47.704513746738655,"d":"47.70"},{"v":41.855427531013405,"d":"41.86"},{"v":36.35618235288556,"d":"36.36"},{"v":31.165895449883553,"d":"31.17"},{"v":26.241537421930747,"d":"26.24"},{"v":21.54032316333086,"d":"21.54"},{"v":17.020932334638733,"d":"17.02"},{"v":12.643962688662345,"d":"12.64"},{"v":8.371907218859867,"d":"8.37"},{"v":4.168849439809683,"d":"4.17"},{"v":0,"d":"0.00"},{"v":-4.168849439809683,"d":"-4.17"},{"v":-8.371907218859867,"d":"-8.37"},{"v":-12.643962688662345,"d":"-12.64"},{"v":-17.020932334638733,"d":"-17.02"},{"v":-21.54032316333086,"d":"-21.54"},{"v":-26.241537421930747,"d":"-26.24"},{"v":-31.165895449883553,"d":"-31.17"},{"v":-36.35618235288556,"d":"-36.36"},{"v":-41.855427531013405,"d":"-41.86"},{"v":-47.704513746738655,"d":"-47.70"},{"v":-53.938123153721385,"d":"-53.94"},{"v":-60.578556843340394,"d":"-60.58"},{"v":-67.62729030678001,"d":"-67.63"},{"v":-75.05498875176778,"d":"-75.05"},{"v":-82.79223117965132,"d":"-82.79"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"},{"v":-78.09992157561065,"d":"-78.10"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":4.602785654653134,"d":"4.60"},{"v":-10.396802061796919,"d":"-10.40"},{"v":-3.9398033161607215,"d":"-3.94"},{"v":-2.872156280028886,"d":"-2.87"},{"v":-2.43445725099279,"d":"-2.43"},{"v":-2.1964179294756927,"d":"-2.20"},{"v":-2.0466793878586484,"d":"-2.05"},{"v":-1.943554982985266,"d":"-1.94"},{"v":-1.8679350553826577,"d":"-1.87"},{"v":-1.8098397525211047,"d":"-1.81"},{"v":-1.7635575209048253,"d":"-1.76"},{"v":-1.725589599025447,"d":"-1.73"},{"v":-1.6936774029657047,"d":"-1.69"},{"v":-1.6663015405257804,"d":"-1.67"},{"v":-1.642406228629819,"d":"-1.64"},{"v":-1.621239819036769,"d":"-1.62"},{"v":-1.6022591261009584,"d":"-1.60"},{"v":-1.5850711045514339,"d":"-1.59"},{"v":-1.5693981517339937,"d":"-1.57"},{"v":-1.555060262570764,"d":"-1.56"},{"v":-1.5419718744771314,"d":"-1.54"},{"v":-1.5301556423034106,"d":"-1.53"},{"v":-1.5197820133902429,"d":"-1.52"},{"v":-1.511257392718174,"d":"-1.51"},{"v":-1.5054193731980683,"d":"-1.51"},{"v":-1.504005070402469,"d":"-1.50"},{"v":-1.510950032867843,"d":"-1.51"},{"v":-1.5369348786391137,"d":"-1.54"},{"v":-1.6234309831717755,"d":"-1.62"},{"v":-2.2294515503189367,"d":"-2.23"},{"v":-0.7660444431189777,"d":"-0.77"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":4.602785654653134,"d":"4.60"},{"v":10.396802061796919,"d":"10.40"},{"v":3.9398033161607215,"d":"3.94"},{"v":2.872156280028886,"d":"2.87"},{"v":2.43445725099279,"d":"2.43"},{"v":2.1964179294756927,"d":"2.20"},{"v":2.0466793878586484,"d":"2.05"},{"v":1.943554982985266,"d":"1.94"},{"v":1.8679350553826577,"d":"1.87"},{"v":1.8098397525211047,"d":"1.81"},{"v":1.7635575209048253,"d":"1.76"},{"v":1.725589599025447,"d":"1.73"},{"v":1.6936774029657047,"d":"1.69"},{"v":1.6663015405257804,"d":"1.67"},{"v":1.642406228629819,"d":"1.64"},{"v":1.621239819036769,"d":"1.62"},{"v":1.6022591261009584,"d":"1.60"},{"v":1.5850711045514339,"d":"1.59"},{"v":1.5693981517339937,"d":"1.57"},{"v":1.555060262570764,"d":"1.56"},{"v":1.5419718744771314,"d":"1.54"},{"v":1.5301556423034106,"d":"1.53"},{"v":1.5197820133902429,"d":"1.52"},{"v":1.511257392718174,"d":"1.51"},{"v":1.5054193731980683,"d":"1.51"},{"v":1.504005070402469,"d":"1.50"},{"v":1.510950032867843,"d":"1.51"},{"v":1.5369348786391137,"d":"1.54"},{"v":1.6234309831717755,"d":"1.62"},{"v":2.2294515503189367,"d":"2.23"},{"v":0.7660444431189777,"d":"0.77"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-31.03103981293868,"d":"-31.03"},{"v":22.00939938344825,"d":"22.01"},{"v":80.9807773909345,"d":"80.98"},{"v":142.20433949235195,"d":"142.20"},{"v":202.48602640607965,"d":"202.49"},{"v":259.44048169741063,"d":"259.44"},{"v":311.5203303988368,"d":"311.52"},{"v":357.8787631897205,"d":"357.88"},{"v":398.1774379103386,"d":"398.18"},{"v":432.4055435051742,"d":"432.41"},{"v":460.73643996109007,"d":"460.74"},{"v":483.4252027974646,"d":"483.43"},{"v":500.7404747105814,"d":"500.74"},{"v":512.9216337141012,"d":"512.92"},{"v":520.1532395836504,"d":"520.15"},{"v":522.5507138915187,"d":"522.55"},{"v":520.1532395836504,"d":"520.15"},{"v":512.9216337141012,"d":"512.92"},{"v":500.7404747105814,"d":"500.74"},{"v":483.4252027974646,"d":"483.43"},{"v":460.73643996109007,"d":"460.74"},{"v":432.4055435051742,"d":"432.41"},{"v":398.1774379103386,"d":"398.18"},{"v":357.8787631897205,"d":"357.88"},{"v":311.5203303988368,"d":"311.52"},{"v":259.44048169741063,"d":"259.44"},{"v":202.48602640607965,"d":"202.49"},{"v":142.20433949235195,"d":"142.20"},{"v":80.9807773909345,"d":"80.98"},{"v":22.00939938344825,"d":"22.01"},{"v":-31.03103981293868,"d":"-31.03"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-16.717056305722647,"d":"-16.72"},{"v":10.701855347785237,"d":"10.70"},{"v":36.115231009789895,"d":"36.12"},{"v":59.015333538920814,"d":"59.02"},{"v":79.18833746366379,"d":"79.19"},{"v":96.6420624439699,"d":"96.64"},{"v":111.52438225976145,"d":"111.52"},{"v":124.05455627720444,"d":"124.05"},{"v":134.47454986378636,"d":"134.47"},{"v":143.0187462877905,"d":"143.02"},{"v":149.89734995919932,"d":"149.90"},{"v":155.28871293926213,"d":"155.29"},{"v":159.33686534360132,"d":"159.34"},{"v":162.1517080845462,"d":"162.15"},{"v":163.81027216307592,"d":"163.81"},{"v":164.35810569345253,"d":"164.36"},{"v":163.81027216307592,"d":"163.81"},{"v":162.1517080845462,"d":"162.15"},{"v":159.33686534360132,"d":"159.34"},{"v":155.28871293926213,"d":"155.29"},{"v":149.89734995919932,"d":"149.90"},{"v":143.0187462877905,"d":"143.02"},{"v":134.47454986378636,"d":"134.47"},{"v":124.05455627720444,"d":"124.05"},{"v":111.52438225976145,"d":"111.52"},{"v":96.6420624439699,"d":"96.64"},{"v":79.18833746366379,"d":"79.19"},{"v":59.015333538920814,"d":"59.02"},{"v":36.115231009789895,"d":"36.12"},{"v":10.701855347785237,"d":"10.70"},{"v":-16.717056305722647,"d":"-16.72"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":117.56229714384068,"d":"117.56"},{"v":176.7614284137962,"d":"176.76"},{"v":238.9318258785076,"d":"238.93"},{"v":300.16295287651786,"d":"300.16"},{"v":357.573366938558,"d":"357.57"},{"v":409.3275847114927,"d":"409.33"},{"v":454.4502024873985,"d":"454.45"},{"v":492.5798687878033,"d":"492.58"},{"v":523.7437294587847,"d":"523.74"},{"v":548.1826149640464,"d":"548.18"},{"v":566.2289139600333,"d":"566.23"},{"v":578.2275784757848,"d":"578.23"},{"v":584.4884674466409,"d":"584.49"},{"v":585.2599092199841,"d":"585.26"},{"v":580.7161192953411,"d":"580.72"},{"v":570.9537715715119,"d":"570.95"},{"v":555.9952734610631,"d":"556.00"},{"v":535.7981935358529,"d":"535.80"},{"v":510.2720160779452,"d":"510.27"},{"v":479.3051342709813,"d":"479.31"},{"v":442.80684057029254,"d":"442.81"},{"v":400.77090613221094,"d":"400.77"},{"v":353.36856129300384,"d":"353.37"},{"v":301.07777488968014,"d":"301.08"},{"v":244.8496480106818,"d":"244.85"},{"v":186.29664716007233,"d":"186.30"},{"v":127.85608476914518,"d":"127.86"},{"v":72.8361180720805,"d":"72.84"},{"v":25.20962158060855,"d":"25.21"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-14.761532197014274,"d":"-14.76"},{"v":9.449976084009617,"d":"9.45"},{"v":31.89055151839882,"d":"31.89"},{"v":52.111850927612075,"d":"52.11"},{"v":69.9250616687669,"d":"69.93"},{"v":85.33708867536517,"d":"85.34"},{"v":98.47850778106421,"d":"98.48"},{"v":109.54292987847371,"d":"109.54"},{"v":118.74401576393291,"d":"118.74"},{"v":126.28873107169767,"d":"126.29"},{"v":132.36269096685234,"d":"132.36"},{"v":137.123384282741,"d":"137.12"},{"v":140.69799281203197,"d":"140.70"},{"v":143.18356150248172,"d":"143.18"},{"v":144.6481104397038,"d":"144.65"},{"v":145.13185962074175,"d":"145.13"},{"v":144.6481104397038,"d":"144.65"},{"v":143.18356150248172,"d":"143.18"},{"v":140.69799281203197,"d":"140.70"},{"v":137.123384282741,"d":"137.12"},{"v":132.36269096685234,"d":"132.36"},{"v":126.28873107169767,"d":"126.29"},{"v":118.74401576393291,"d":"118.74"},{"v":109.54292987847371,"d":"109.54"},{"v":98.47850778106421,"d":"98.48"},{"v":85.33708867536517,"d":"85.34"},{"v":69.9250616687669,"d":"69.93"},{"v":52.111850927612075,"d":"52.11"},{"v":31.89055151839882,"d":"31.89"},{"v":9.449976084009617,"d":"9.45"},{"v":-14.761532197014274,"d":"-14.76"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-14.761532197014274,"d":"-14.76"},{"v":127.0122732278503,"d":"127.01"},{"v":208.65197993219502,"d":"208.65"},{"v":291.04367680611966,"d":"291.04"},{"v":370.08801454528475,"d":"370.09"},{"v":442.9104556139232,"d":"442.91"},{"v":507.8060924925569,"d":"507.81"},{"v":563.9931323658722,"d":"563.99"},{"v":611.3238845517362,"d":"611.32"},{"v":650.0324605304825,"d":"650.03"},{"v":680.5453059308987,"d":"680.55"},{"v":703.3522982427743,"d":"703.35"},{"v":718.9255712878168,"d":"718.93"},{"v":727.6720289491227,"d":"727.67"},{"v":729.908019659688,"d":"729.91"},{"v":725.8479789160829,"d":"725.85"},{"v":715.6018820112157,"d":"715.60"},{"v":699.1788349635449,"d":"699.18"},{"v":676.4961863478849,"d":"676.50"},{"v":647.3954003606862,"d":"647.40"},{"v":611.6678252378337,"d":"611.67"},{"v":569.0955716419902,"d":"569.10"},{"v":519.5149218961438,"d":"519.51"},{"v":462.91149117147756,"d":"462.91"},{"v":399.55628267074434,"d":"399.56"},{"v":330.18673668604697,"d":"330.19"},{"v":256.2217088288392,"d":"256.22"},{"v":179.96793569675725,"d":"179.97"},{"v":104.72666959047932,"d":"104.73"},{"v":34.65959766461817,"d":"34.66"},{"v":-14.761532197014274,"d":"-14.76"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":117.56229714384068,"d":"117.56"},{"v":176.7614284137962,"d":"176.76"},{"v":238.9318258785076,"d":"238.93"},{"v":300.16295287651786,"d":"300.16"},{"v":357.573366938558,"d":"357.57"},{"v":409.3275847114927,"d":"409.33"},{"v":454.4502024873985,"d":"454.45"},{"v":492.5798687878033,"d":"492.58"},{"v":523.7437294587847,"d":"523.74"},{"v":548.1826149640464,"d":"548.18"},{"v":566.2289139600333,"d":"566.23"},{"v":578.2275784757848,"d":"578.23"},{"v":584.4884674466409,"d":"584.49"},{"v":585.2599092199841,"d":"585.26"},{"v":580.7161192953411,"d":"580.72"},{"v":570.9537715715119,"d":"570.95"},{"v":555.9952734610631,"d":"556.00"},{"v":535.7981935358529,"d":"535.80"},{"v":510.2720160779452,"d":"510.27"},{"v":479.3051342709813,"d":"479.31"},{"v":442.80684057029254,"d":"442.81"},{"v":400.77090613221094,"d":"400.77"},{"v":353.36856129300384,"d":"353.37"},{"v":301.07777488968014,"d":"301.08"},{"v":244.8496480106818,"d":"244.85"},{"v":186.29664716007233,"d":"186.30"},{"v":127.85608476914518,"d":"127.86"},{"v":72.8361180720805,"d":"72.84"},{"v":25.20962158060855,"d":"25.21"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-14.761532197014274,"d":"-14.76"},{"v":127.0122732278503,"d":"127.01"},{"v":208.65197993219502,"d":"208.65"},{"v":291.04367680611966,"d":"291.04"},{"v":370.08801454528475,"d":"370.09"},{"v":442.9104556139232,"d":"442.91"},{"v":507.8060924925569,"d":"507.81"},{"v":563.9931323658722,"d":"563.99"},{"v":611.3238845517362,"d":"611.32"},{"v":650.0324605304825,"d":"650.03"},{"v":680.5453059308987,"d":"680.55"},{"v":703.3522982427743,"d":"703.35"},{"v":718.9255712878168,"d":"718.93"},{"v":727.6720289491227,"d":"727.67"},{"v":729.908019659688,"d":"729.91"},{"v":725.8479789160829,"d":"725.85"},{"v":715.6018820112157,"d":"715.60"},{"v":699.1788349635449,"d":"699.18"},{"v":676.4961863478849,"d":"676.50"},{"v":647.3954003606862,"d":"647.40"},{"v":611.6678252378337,"d":"611.67"},{"v":569.0955716419902,"d":"569.10"},{"v":519.5149218961438,"d":"519.51"},{"v":462.91149117147756,"d":"462.91"},{"v":399.55628267074434,"d":"399.56"},{"v":330.18673668604697,"d":"330.19"},{"v":256.2217088288392,"d":"256.22"},{"v":179.96793569675725,"d":"179.97"},{"v":104.72666959047932,"d":"104.73"},{"v":34.65959766461817,"d":"34.66"},{"v":-14.761532197014274,"d":"-14.76"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":11321.59345145366,"d":"11,322"},"W/m2"]
[null,"Total Directa disponible",{"v":11321.59345145366,"d":"11,322"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":14236.77115342664,"d":"14,237"}]
[null,"Total global ",{"v":14236.77115342664,"d":"14,237"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.2047639644240069,"d":"0.205"},{"v":0.33894926514481216,"d":"0.339"}]
[]
[null,"MARZO"]
[null,"Declinacion dia tipo",{"v":-2.8188786528898215,"d":"-2.82"},{"v":-0.04919871370710976,"d":"-0.05"}]
[null,"ocaso",{"v":-87.59830543454483,"d":"-87.60"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"},{"v":0.06374760666673022,"d":"0.064"}]
[null,"c",{"v":-0.5775220327470586,"d":"-0.578"},{"v":-0.5731167323770817,"d":"-0.573"},{"v":-0.5600346840897029,"d":"-0.560"},{"v":-0.5386733793022986,"d":"-0.539"},{"v":-0.5096818704514924,"d":"-0.510"},{"v":-0.4739410498633045,"d":"-0.474"},{"v":-0.43253688428557924,"d":"-0.433"},{"v":-0.38672741833787666,"d":"-0.387"},{"v":-0.33790454946231013,"d":"-0.338"},{"v":-0.28755173582409976,"d":"-0.288"},{"v":-0.23719892218588934,"d":"-0.237"},{"v":-0.1883760533103226,"d":"-0.188"},{"v":-0.14256658736262032,"d":"-0.143"},{"v":-0.10116242178489505,"d":"-0.101"},{"v":-0.06542160119670719,"d":"-0.065"},{"v":-0.036430092345900944,"d":"-0.036"},{"v":-0.015068787558496702,"d":"-0.015"},{"v":-0.0019867392711180555,"d":"-0.002"},{"v":0.002418561098858905,"d":"0.002"},{"v":-0.001986739271118045,"d":"-0.002"},{"v":-0.015068787558496723,"d":"-0.015"},{"v":-0.03643009234590091,"d":"-0.036"},{"v":-0.06542160119670723,"d":"-0.065"},{"v":-0.10116242178489511,"d":"-0.101"},{"v":-0.1425665873626205,"d":"-0.143"},{"v":-0.1883760533103228,"d":"-0.188"},{"v":-0.23719892218588934,"d":"-0.237"},{"v":-0.2875517358240999,"d":"-0.288"},{"v":-0.3379045494623103,"d":"-0.338"},{"v":-0.3867274183378769,"d":"-0.387"},{"v":-0.43253688428557924,"d":"-0.433"},{"v":-0.4739410498633045,"d":"-0.474"},{"v":-0.5096818704514925,"d":"-0.510"},{"v":-0.5386733793022989,"d":"-0.539"},{"v":-0.5600346840897029,"d":"-0.560"},{"v":-0.5731167323770817,"d":"-0.573"},{"v":-0.5775220327470586,"d":"-0.578"},{"v":-0.5731167323770817,"d":"-0.573"},{"v":-0.5600346840897029,"d":"-0.560"},{"v":-0.5386733793022989,"d":"-0.539"},{"v":-0.5096818704514925,"d":"-0.510"},{"v":-0.4739410498633045,"d":"-0.474"},{"v":-0.43253688428557924,"d":"-0.433"},{"v":-0.3867274183378769,"d":"-0.387"},{"v":-0.3379045494623103,"d":"-0.338"},{"v":-0.2875517358240999,"d":"-0.288"},{"v":-0.23719892218588934,"d":"-0.237"},{"v":-0.1883760533103228,"d":"-0.188"},{"v":-0.1425665873626205,"d":"-0.143"},{"v":-0.10116242178489511,"d":"-0.101"},{"v":-0.06542160119670723,"d":"-0.065"},{"v":-0.03643009234590091,"d":"-0.036"},{"v":-0.015068787558496723,"d":"-0.015"},{"v":-0.001986739271118045,"d":"-0.002"},{"v":0.002418561098858905,"d":"0.002"},{"v":-0.0019867392711180555,"d":"-0.002"},{"v":-0.015068787558496702,"d":"-0.015"},{"v":-0.036430092345900944,"d":"-0.036"},{"v":-0.06542160119670719,"d":"-0.065"},{"v":-0.10116242178489505,"d":"-0.101"},{"v":-0.14256658736262032,"d":"-0.143"},{"v":-0.1883760533103226,"d":"-0.188"},{"v":-0.23719892218588934,"d":"-0.237"},{"v":-0.28755173582409976,"d":"-0.288"},{"v":-0.33790454946231013,"d":"-0.338"},{"v":-0.38672741833787666,"d":"-0.387"},{"v":-0.43253688428557924,"d":"-0.433"},{"v":-0.4739410498633045,"d":"-0.474"},{"v":-0.5096818704514924,"d":"-0.510"},{"v":-0.5386733793022986,"d":"-0.539"},{"v":-0.5600346840897029,"d":"-0.560"},{"v":-0.5731167323770817,"d":"-0.573"},{"v":-0.5775220327470586,"d":"-0.578"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1.518082172878121,"d":"1.52"},{"v":7.268374699142503,"d":"7.27"},{"v":12.751976364189883,"d":"12.75"},{"v":17.856487763957453,"d":"17.86"},{"v":22.51093359144924,"d":"22.51"},{"v":26.6829519351283,"d":"26.68"},{"v":30.370392560673285,"d":"30.37"},{"v":33.591388987359025,"d":"33.59"},{"v":36.37554242979789,"d":"36.38"},{"v":38.75727809926255,"d":"38.76"},{"v":40.771397934735084,"d":"40.77"},{"v":42.45039548405709,"d":"42.45"},{"v":43.82300817888524,"d":"43.82"},{"v":44.913557390825645,"d":"44.91"},{"v":45.741745518459275,"d":"45.74"},{"v":46.32268766406998,"d":"46.32"},{"v":46.667037281329414,"d":"46.67"},{"v":46.78112134711019,"d":"46.78"},{"v":46.667037281329414,"d":"46.67"},{"v":46.32268766406998,"d":"46.32"},{"v":45.741745518459275,"d":"45.74"},{"v":44.913557390825645,"d":"44.91"},{"v":43.82300817888524,"d":"43.82"},{"v":42.45039548405709,"d":"42.45"},{"v":40.771397934735084,"d":"40.77"},{"v":38.75727809926255,"d":"38.76"},{"v":36.37554242979789,"d":"36.38"},{"v":33.591388987359025,"d":"33.59"},{"v":30.370392560673285,"d":"30.37"},{"v":26.6829519351283,"d":"26.68"},{"v":22.51093359144924,"d":"22.51"},{"v":17.856487763957453,"d":"17.86"},{"v":12.751976364189883,"d":"12.75"},{"v":7.268374699142503,"d":"7.27"},{"v":1.518082172878121,"d":"1.52"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",74]
[null,"Declinacion . radianes",{"v":-0.04919871370710976,"d":"-0.049"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.5288788490004492,"d":"1.529"}]
[null,"Distancia sol - tierra. Bo",{"v":1.0329918443564325,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":0.7112175202699583,"d":"0.711"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":7672.364423858824,"d":"7,672"}]
[null,"H1",{"v":37958.21082117033,"d":"37,958"}]
[null,"H2",{"v":0.7599487040235403,"d":"0.760"}]
[null,"H3",{"v":-0.04873118375358194,"d":"-0.049"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":4656.716666666666,"d":"4,657"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.6069467519276888,"d":"0.607"}]
[null,"Fraccion difusa diaria promedio",{"v":0.34885335265563017,"d":"0.349"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.6413761441120339,"d":"0.641"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.4400592745251065,"d":"0.440"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1.518082172878121,"d":"1.52"},{"v":7.268374699142503,"d":"7.27"},{"v":12.751976364189883,"d":"12.75"},{"v":17.856487763957453,"d":"17.86"},{"v":22.51093359144924,"d":"22.51"},{"v":26.6829519351283,"d":"26.68"},{"v":30.370392560673285,"d":"30.37"},{"v":33.591388987359025,"d":"33.59"},{"v":36.37554242979789,"d":"36.38"},{"v":38.75727809926255,"d":"38.76"},{"v":40.771397934735084,"d":"40.77"},{"v":42.45039548405709,"d":"42.45"},{"v":43.82300817888524,"d":"43.82"},{"v":44.913557390825645,"d":"44.91"},{"v":45.741745518459275,"d":"45.74"},{"v":46.32268766406998,"d":"46.32"},{"v":46.667037281329414,"d":"46.67"},{"v":46.78112134711019,"d":"46.78"},{"v":46.667037281329414,"d":"46.67"},{"v":46.32268766406998,"d":"46.32"},{"v":45.741745518459275,"d":"45.74"},{"v":44.913557390825645,"d":"44.91"},{"v":43.82300817888524,"d":"43.82"},{"v":42.45039548405709,"d":"42.45"},{"v":40.771397934735084,"d":"40.77"},{"v":38.75727809926255,"d":"38.76"},{"v":36.37554242979789,"d":"36.38"},{"v":33.591388987359025,"d":"33.59"},{"v":30.370392560673285,"d":"30.37"},{"v":26.6829519351283,"d":"26.68"},{"v":22.51093359144924,"d":"22.51"},{"v":17.856487763957453,"d":"17.86"},{"v":12.751976364189883,"d":"12.75"},{"v":7.268374699142503,"d":"7.27"},{"v":1.518082172878121,"d":"1.52"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":87.59830543454483,"d":"87.60"},{"v":85.59905930541211,"d":"85.60"},{"v":77.98076441852082,"d":"77.98"},{"v":70.60339153202894,"d":"70.60"},{"v":63.57387115001644,"d":"63.57"},{"v":56.95760359634805,"d":"56.96"},{"v":50.78105860167394,"d":"50.78"},{"v":45.03999067492083,"d":"45.04"},{"v":39.7092079741178,"d":"39.71"},{"v":34.75124751664268,"d":"34.75"},{"v":30.122882939045162,"d":"30.12"},{"v":25.779427816379417,"d":"25.78"},{"v":21.67725788304838,"d":"21.68"},{"v":17.77506783464038,"d":"17.78"},{"v":14.034304377420293,"d":"14.03"},{"v":10.419098739566667,"d":"10.42"},{"v":6.895913503726315,"d":"6.90"},{"v":3.4330366734285853,"d":"3.43"},{"v":0,"d":"0.00"},{"v":-3.4330366734285853,"d":"-3.43"},{"v":-6.895913503726315,"d":"-6.90"},{"v":-10.419098739566667,"d":"-10.42"},{"v":-14.034304377420293,"d":"-14.03"},{"v":-17.77506783464038,"d":"-17.78"},{"v":-21.67725788304838,"d":"-21.68"},{"v":-25.779427816379417,"d":"-25.78"},{"v":-30.122882939045162,"d":"-30.12"},{"v":-34.75124751664268,"d":"-34.75"},{"v":-39.7092079741178,"d":"-39.71"},{"v":-45.03999067492083,"d":"-45.04"},{"v":-50.78105860167394,"d":"-50.78"},{"v":-56.95760359634805,"d":"-56.96"},{"v":-63.57387115001644,"d":"-63.57"},{"v":-70.60339153202894,"d":"-70.60"},{"v":-77.98076441852082,"d":"-77.98"},{"v":-85.59905930541211,"d":"-85.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"},{"v":-87.59830543454483,"d":"-87.60"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-9.06158880319973,"d":"-9.06"},{"v":-2.895961216853907,"d":"-2.90"},{"v":-2.186173111880993,"d":"-2.19"},{"v":-1.9104948020209138,"d":"-1.91"},{"v":-1.7630011907841048,"d":"-1.76"},{"v":-1.6704261071688842,"d":"-1.67"},{"v":-1.6063210739780223,"d":"-1.61"},{"v":-1.558810496107988,"d":"-1.56"},{"v":-1.5217689817266924,"d":"-1.52"},{"v":-1.4917145614783849,"d":"-1.49"},{"v":-1.4665181940512209,"d":"-1.47"},{"v":-1.4448005258941996,"d":"-1.44"},{"v":-1.4256235105124837,"d":"-1.43"},{"v":-1.4083211500546828,"d":"-1.41"},{"v":-1.3924009205104981,"d":"-1.39"},{"v":-1.3774832476384626,"d":"-1.38"},{"v":-1.3632623679187739,"d":"-1.36"},{"v":-1.3494795132730666,"d":"-1.35"},{"v":-1.3359031543434874,"d":"-1.34"},{"v":-1.322312962610089,"d":"-1.32"},{"v":-1.308485064364968,"d":"-1.31"},{"v":-1.2941764222324934,"d":"-1.29"},{"v":-1.279105878540201,"d":"-1.28"},{"v":-1.2629283816568668,"d":"-1.26"},{"v":-1.2451967084984066,"d":"-1.25"},{"v":-1.225300433642867,"d":"-1.23"},{"v":-1.2023622089173478,"d":"-1.20"},{"v":-1.1750496010955496,"d":"-1.18"},{"v":-1.1412074461289539,"d":"-1.14"},{"v":-1.0970711068780876,"d":"-1.10"},{"v":-1.0353709202258128,"d":"-1.04"},{"v":-0.9399452778577244,"d":"-0.94"},{"v":-0.7660444431189783,"d":"-0.77"},{"v":-0.3267958464280462,"d":"-0.33"},{"v":3.4457138085333696,"d":"3.45"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":9.06158880319973,"d":"9.06"},{"v":2.895961216853907,"d":"2.90"},{"v":2.186173111880993,"d":"2.19"},{"v":1.9104948020209138,"d":"1.91"},{"v":1.7630011907841048,"d":"1.76"},{"v":1.6704261071688842,"d":"1.67"},{"v":1.6063210739780223,"d":"1.61"},{"v":1.558810496107988,"d":"1.56"},{"v":1.5217689817266924,"d":"1.52"},{"v":1.4917145614783849,"d":"1.49"},{"v":1.4665181940512209,"d":"1.47"},{"v":1.4448005258941996,"d":"1.44"},{"v":1.4256235105124837,"d":"1.43"},{"v":1.4083211500546828,"d":"1.41"},{"v":1.3924009205104981,"d":"1.39"},{"v":1.3774832476384626,"d":"1.38"},{"v":1.3632623679187739,"d":"1.36"},{"v":1.3494795132730666,"d":"1.35"},{"v":1.3359031543434874,"d":"1.34"},{"v":1.322312962610089,"d":"1.32"},{"v":1.308485064364968,"d":"1.31"},{"v":1.2941764222324934,"d":"1.29"},{"v":1.279105878540201,"d":"1.28"},{"v":1.2629283816568668,"d":"1.26"},{"v":1.2451967084984066,"d":"1.25"},{"v":1.225300433642867,"d":"1.23"},{"v":1.2023622089173478,"d":"1.20"},{"v":1.1750496010955496,"d":"1.18"},{"v":1.1412074461289539,"d":"1.14"},{"v":1.0970711068780876,"d":"1.10"},{"v":1.0353709202258128,"d":"1.04"},{"v":0.9399452778577244,"d":"0.94"},{"v":0.7660444431189783,"d":"0.77"},{"v":0.3267958464280462,"d":"0.33"},{"v":3.4457138085333696,"d":"3.45"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":15.329726860189457,"d":"15.33"},{"v":79.48360528952605,"d":"79.48"},{"v":148.98490478058983,"d":"148.98"},{"v":220.02730976056424,"d":"220.03"},{"v":289.19488362942127,"d":"289.19"},{"v":353.933603285583,"d":"353.93"},{"v":412.66649085169223,"d":"412.67"},{"v":464.6623753619803,"d":"464.66"},{"v":509.80313478863275,"d":"509.80"},{"v":548.3519074840592,"d":"548.35"},{"v":580.7692506001151,"d":"580.77"},{"v":607.5861380823477,"d":"607.59"},{"v":629.3249051352824,"d":"629.32"},{"v":646.4545557126579,"d":"646.45"},{"v":659.3681774094745,"d":"659.37"},{"v":668.3733137393289,"d":"668.37"},{"v":673.6891377220244,"d":"673.69"},{"v":675.4465754531102,"d":"675.45"},{"v":673.6891377220244,"d":"673.69"},{"v":668.3733137393289,"d":"668.37"},{"v":659.3681774094745,"d":"659.37"},{"v":646.4545557126579,"d":"646.45"},{"v":629.3249051352824,"d":"629.32"},{"v":607.5861380823477,"d":"607.59"},{"v":580.7692506001151,"d":"580.77"},{"v":548.3519074840592,"d":"548.35"},{"v":509.80313478863275,"d":"509.80"},{"v":464.6623753619803,"d":"464.66"},{"v":412.66649085169223,"d":"412.67"},{"v":353.933603285583,"d":"353.93"},{"v":289.19488362942127,"d":"289.19"},{"v":220.02730976056424,"d":"220.03"},{"v":148.98490478058983,"d":"148.98"},{"v":79.48360528952605,"d":"79.48"},{"v":15.329726860189457,"d":"15.33"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":7.921013132479198,"d":"7.92"},{"v":37.82754185378224,"d":"37.83"},{"v":65.99672505152395,"d":"66.00"},{"v":91.68092946898196,"d":"91.68"},{"v":114.47181928023276,"d":"114.47"},{"v":134.2630960324267,"d":"134.26"},{"v":151.16653320340936,"d":"151.17"},{"v":165.42196183174988,"d":"165.42"},{"v":177.32448274779122,"d":"177.32"},{"v":187.175441301941,"d":"187.18"},{"v":195.25422175482075,"d":"195.25"},{"v":201.80483254969738,"d":"201.80"},{"v":207.03159530175978,"d":"207.03"},{"v":211.09973544662506,"d":"211.10"},{"v":214.13816154340296,"d":"214.14"},{"v":216.242838996567,"d":"216.24"},{"v":217.47989241758876,"d":"217.48"},{"v":217.88800174820636,"d":"217.89"},{"v":217.47989241758876,"d":"217.48"},{"v":216.242838996567,"d":"216.24"},{"v":214.13816154340296,"d":"214.14"},{"v":211.09973544662506,"d":"211.10"},{"v":207.03159530175978,"d":"207.03"},{"v":201.80483254969738,"d":"201.80"},{"v":195.25422175482075,"d":"195.25"},{"v":187.175441301941,"d":"187.18"},{"v":177.32448274779122,"d":"177.32"},{"v":165.42196183174988,"d":"165.42"},{"v":151.16653320340936,"d":"151.17"},{"v":134.2630960324267,"d":"134.26"},{"v":114.47181928023276,"d":"114.47"},{"v":91.68092946898196,"d":"91.68"},{"v":65.99672505152395,"d":"66.00"},{"v":37.82754185378224,"d":"37.83"},{"v":7.921013132479198,"d":"7.92"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":181.4265271276311,"d":"181.43"},{"v":245.2050924052674,"d":"245.21"},{"v":308.03697050506713,"d":"308.04"},{"v":366.943350290704,"d":"366.94"},{"v":420.0528928147971,"d":"420.05"},{"v":466.45909747061796,"d":"466.46"},{"v":505.95569976205473,"d":"505.96"},{"v":538.7721938671713,"d":"538.77"},{"v":565.3648038818055,"d":"565.36"},{"v":586.2730436316081,"d":"586.27"},{"v":602.0312708308024,"d":"602.03"},{"v":613.1194011589091,"d":"613.12"},{"v":619.9386839308218,"d":"619.94"},{"v":622.8021547049796,"d":"622.80"},{"v":621.9328960201617,"d":"621.93"},{"v":617.4659213372122,"d":"617.47"},{"v":609.4513698428574,"d":"609.45"},{"v":597.8579875434074,"d":"597.86"},{"v":582.5768259677324,"d":"582.58"},{"v":563.4259436935646,"d":"563.43"},{"v":540.1578550762572,"d":"540.16"},{"v":512.4727275029607,"d":"512.47"},{"v":480.04204499482887,"d":"480.04"},{"v":442.54968063454777,"d":"442.55"},{"v":399.7597664856885,"d":"399.76"},{"v":351.6223285503645,"d":"351.62"},{"v":298.4256988306265,"d":"298.43"},{"v":240.99416654069117,"d":"240.99"},{"v":180.90317991989323,"d":"180.90"},{"v":120.63857408520447,"d":"120.64"},{"v":63.572633926009956,"d":"63.57"},{"v":13.613028509344286,"d":"13.61"},{"v":25.528307195041975,"d":"25.53"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":58.27657477064746,"d":"58.28"},{"v":80.95629801433927,"d":"80.96"},{"v":101.08116016678747,"d":"101.08"},{"v":118.55729733200842,"d":"118.56"},{"v":133.4834079747208,"d":"133.48"},{"v":146.07126823140078,"d":"146.07"},{"v":156.58145869284186,"d":"156.58"},{"v":165.28007399981766,"d":"165.28"},{"v":172.41381666281092,"d":"172.41"},{"v":178.19815155947444,"d":"178.20"},{"v":182.813499216365,"d":"182.81"},{"v":186.40575736469927,"d":"186.41"},{"v":189.0887551267204,"d":"189.09"},{"v":190.9472320870795,"d":"190.95"},{"v":192.0395777470979,"d":"192.04"},{"v":192.399947354859,"d":"192.40"},{"v":192.0395777470979,"d":"192.04"},{"v":190.9472320870795,"d":"190.95"},{"v":189.0887551267204,"d":"189.09"},{"v":186.40575736469927,"d":"186.41"},{"v":182.813499216365,"d":"182.81"},{"v":178.19815155947444,"d":"178.20"},{"v":172.41381666281092,"d":"172.41"},{"v":165.28007399981766,"d":"165.28"},{"v":156.58145869284186,"d":"156.58"},{"v":146.07126823140078,"d":"146.07"},{"v":133.4834079747208,"d":"133.48"},{"v":118.55729733200842,"d":"118.56"},{"v":101.08116016678747,"d":"101.08"},{"v":80.95629801433927,"d":"80.96"},{"v":58.27657477064746,"d":"58.28"},{"v":33.40256004386134,"d":"33.40"},{"v":6.994430613243668,"d":"6.99"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":239.70310189827853,"d":"239.70"},{"v":326.1613904196067,"d":"326.16"},{"v":409.1181306718546,"d":"409.12"},{"v":485.50064762271245,"d":"485.50"},{"v":553.5363007895179,"d":"553.54"},{"v":612.5303657020188,"d":"612.53"},{"v":662.5371584548966,"d":"662.54"},{"v":704.0522678669889,"d":"704.05"},{"v":737.7786205446164,"d":"737.78"},{"v":764.4711951910825,"d":"764.47"},{"v":784.8447700471675,"d":"784.84"},{"v":799.5251585236084,"d":"799.53"},{"v":809.0274390575421,"d":"809.03"},{"v":813.7493867920591,"d":"813.75"},{"v":813.9724737672595,"d":"813.97"},{"v":809.8658686920712,"d":"809.87"},{"v":801.4909475899553,"d":"801.49"},{"v":788.8052196304868,"d":"788.81"},{"v":771.6655810944528,"d":"771.67"},{"v":749.8317010582639,"d":"749.83"},{"v":722.9713542926222,"d":"722.97"},{"v":690.6708790624351,"d":"690.67"},{"v":652.4558616576398,"d":"652.46"},{"v":607.8297546343654,"d":"607.83"},{"v":556.3412251785303,"d":"556.34"},{"v":497.6935967817653,"d":"497.69"},{"v":431.9091068053473,"d":"431.91"},{"v":359.55146387269957,"d":"359.55"},{"v":281.98434008668073,"d":"281.98"},{"v":201.59487209954375,"d":"201.59"},{"v":121.84920869665741,"d":"121.85"},{"v":47.01558855320563,"d":"47.02"},{"v":32.52273780828564,"d":"32.52"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":181.4265271276311,"d":"181.43"},{"v":245.2050924052674,"d":"245.21"},{"v":308.03697050506713,"d":"308.04"},{"v":366.943350290704,"d":"366.94"},{"v":420.0528928147971,"d":"420.05"},{"v":466.45909747061796,"d":"466.46"},{"v":505.95569976205473,"d":"505.96"},{"v":538.7721938671713,"d":"538.77"},{"v":565.3648038818055,"d":"565.36"},{"v":586.2730436316081,"d":"586.27"},{"v":602.0312708308024,"d":"602.03"},{"v":613.1194011589091,"d":"613.12"},{"v":619.9386839308218,"d":"619.94"},{"v":622.8021547049796,"d":"622.80"},{"v":621.9328960201617,"d":"621.93"},{"v":617.4659213372122,"d":"617.47"},{"v":609.4513698428574,"d":"609.45"},{"v":597.8579875434074,"d":"597.86"},{"v":582.5768259677324,"d":"582.58"},{"v":563.4259436935646,"d":"563.43"},{"v":540.1578550762572,"d":"540.16"},{"v":512.4727275029607,"d":"512.47"},{"v":480.04204499482887,"d":"480.04"},{"v":442.54968063454777,"d":"442.55"},{"v":399.7597664856885,"d":"399.76"},{"v":351.6223285503645,"d":"351.62"},{"v":298.4256988306265,"d":"298.43"},{"v":240.99416654069117,"d":"240.99"},{"v":180.90317991989323,"d":"180.90"},{"v":120.63857408520447,"d":"120.64"},{"v":63.572633926009956,"d":"63.57"},{"v":13.613028509344286,"d":"13.61"},{"v":25.528307195041975,"d":"25.53"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":239.70310189827853,"d":"239.70"},{"v":326.1613904196067,"d":"326.16"},{"v":409.1181306718546,"d":"409.12"},{"v":485.50064762271245,"d":"485.50"},{"v":553.5363007895179,"d":"553.54"},{"v":612.5303657020188,"d":"612.53"},{"v":662.5371584548966,"d":"662.54"},{"v":704.0522678669889,"d":"704.05"},{"v":737.7786205446164,"d":"737.78"},{"v":764.4711951910825,"d":"764.47"},{"v":784.8447700471675,"d":"784.84"},{"v":799.5251585236084,"d":"799.53"},{"v":809.0274390575421,"d":"809.03"},{"v":813.7493867920591,"d":"813.75"},{"v":813.9724737672595,"d":"813.97"},{"v":809.8658686920712,"d":"809.87"},{"v":801.4909475899553,"d":"801.49"},{"v":788.8052196304868,"d":"788.81"},{"v":771.6655810944528,"d":"771.67"},{"v":749.8317010582639,"d":"749.83"},{"v":722.9713542926222,"d":"722.97"},{"v":690.6708790624351,"d":"690.67"},{"v":652.4558616576398,"d":"652.46"},{"v":607.8297546343654,"d":"607.83"},{"v":556.3412251785303,"d":"556.34"},{"v":497.6935967817653,"d":"497.69"},{"v":431.9091068053473,"d":"431.91"},{"v":359.55146387269957,"d":"359.55"},{"v":281.98434008668073,"d":"281.98"},{"v":201.59487209954375,"d":"201.59"},{"v":121.84920869665741,"d":"121.85"},{"v":47.01558855320563,"d":"47.02"},{"v":32.52273780828564,"d":"32.52"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":13905.372119038626,"d":"13,905"},"W/m2"]
[null,"Total Directa disponible",{"v":13905.372119038626,"d":"13,905"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":18642.557714944214,"d":"18,643"}]
[null,"Total global ",{"v":18642.557714944214,"d":"18,643"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.2541059906231736,"d":"0.254"},{"v":0.34885335265563017,"d":"0.349"}]
[]
[null,"ABRIL"]
[null,"Declinacion dia tipo",{"v":9.414893346880055,"d":"9.41"},{"v":0.16432088762716554,"d":"0.16"}]
[null,"ocaso",{"v":-98.1126886179493,"d":"-98.11"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"},{"v":-0.21204202332414074,"d":"-0.212"}]
[null,"c",{"v":-0.5531813908637427,"d":"-0.553"},{"v":-0.5487760904937659,"d":"-0.549"},{"v":-0.535694042206387,"d":"-0.536"},{"v":-0.5143327374189828,"d":"-0.514"},{"v":-0.4853412285681765,"d":"-0.485"},{"v":-0.4496004079799887,"d":"-0.450"},{"v":-0.40819624240226343,"d":"-0.408"},{"v":-0.36238677645456085,"d":"-0.362"},{"v":-0.3135639075789943,"d":"-0.314"},{"v":-0.26321109394078396,"d":"-0.263"},{"v":-0.21285828030257353,"d":"-0.213"},{"v":-0.16403541142700678,"d":"-0.164"},{"v":-0.11822594547930453,"d":"-0.118"},{"v":-0.07682177990157926,"d":"-0.077"},{"v":-0.041080959313391396,"d":"-0.041"},{"v":-0.012089450462585149,"d":"-0.012"},{"v":0.009271854324819095,"d":"0.009"},{"v":0.022353902612197742,"d":"0.022"},{"v":0.026759202982174702,"d":"0.027"},{"v":0.022353902612197753,"d":"0.022"},{"v":0.009271854324819074,"d":"0.009"},{"v":-0.012089450462585114,"d":"-0.012"},{"v":-0.04108095931339144,"d":"-0.041"},{"v":-0.07682177990157932,"d":"-0.077"},{"v":-0.11822594547930472,"d":"-0.118"},{"v":-0.164035411427007,"d":"-0.164"},{"v":-0.21285828030257353,"d":"-0.213"},{"v":-0.26321109394078407,"d":"-0.263"},{"v":-0.3135639075789945,"d":"-0.314"},{"v":-0.3623867764545611,"d":"-0.362"},{"v":-0.40819624240226343,"d":"-0.408"},{"v":-0.4496004079799887,"d":"-0.450"},{"v":-0.48534122856817663,"d":"-0.485"},{"v":-0.514332737418983,"d":"-0.514"},{"v":-0.535694042206387,"d":"-0.536"},{"v":-0.5487760904937659,"d":"-0.549"},{"v":-0.5531813908637427,"d":"-0.553"},{"v":-0.5487760904937659,"d":"-0.549"},{"v":-0.535694042206387,"d":"-0.536"},{"v":-0.514332737418983,"d":"-0.514"},{"v":-0.48534122856817663,"d":"-0.485"},{"v":-0.4496004079799887,"d":"-0.450"},{"v":-0.40819624240226343,"d":"-0.408"},{"v":-0.3623867764545611,"d":"-0.362"},{"v":-0.3135639075789945,"d":"-0.314"},{"v":-0.26321109394078407,"d":"-0.263"},{"v":-0.21285828030257353,"d":"-0.213"},{"v":-0.164035411427007,"d":"-0.164"},{"v":-0.11822594547930472,"d":"-0.118"},{"v":-0.07682177990157932,"d":"-0.077"},{"v":-0.04108095931339144,"d":"-0.041"},{"v":-0.012089450462585114,"d":"-0.012"},{"v":0.009271854324819074,"d":"0.009"},{"v":0.022353902612197753,"d":"0.022"},{"v":0.026759202982174702,"d":"0.027"},{"v":0.022353902612197742,"d":"0.022"},{"v":0.009271854324819095,"d":"0.009"},{"v":-0.012089450462585149,"d":"-0.012"},{"v":-0.041080959313391396,"d":"-0.041"},{"v":-0.07682177990157926,"d":"-0.077"},{"v":-0.11822594547930453,"d":"-0.118"},{"v":-0.16403541142700678,"d":"-0.164"},{"v":-0.21285828030257353,"d":"-0.213"},{"v":-0.26321109394078396,"d":"-0.263"},{"v":-0.3135639075789943,"d":"-0.314"},{"v":-0.36238677645456085,"d":"-0.362"},{"v":-0.40819624240226343,"d":"-0.408"},{"v":-0.4496004079799887,"d":"-0.450"},{"v":-0.4853412285681765,"d":"-0.485"},{"v":-0.5143327374189828,"d":"-0.514"},{"v":-0.535694042206387,"d":"-0.536"},{"v":-0.5487760904937659,"d":"-0.549"},{"v":-0.5531813908637427,"d":"-0.553"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":8.849897158602623,"d":"8.85"},{"v":14.619297938370392,"d":"14.62"},{"v":20.38869871813815,"d":"20.39"},{"v":25.849911536808456,"d":"25.85"},{"v":30.88877569320852,"d":"30.89"},{"v":35.43780548044363,"d":"35.44"},{"v":39.47293991781649,"d":"39.47"},{"v":43.00332869995458,"d":"43.00"},{"v":46.05929666412984,"d":"46.06"},{"v":48.68191256645686,"d":"48.68"},{"v":50.91547110294917,"d":"50.92"},{"v":52.8027975888045,"d":"52.80"},{"v":54.3827079930633,"d":"54.38"},{"v":55.68889306298975,"d":"55.69"},{"v":56.74964150205397,"d":"56.75"},{"v":57.58800012007108,"d":"57.59"},{"v":58.22211979914286,"d":"58.22"},{"v":58.665641195648135,"d":"58.67"},{"v":58.92804035961495,"d":"58.93"},{"v":59.01489334688005,"d":"59.01"},{"v":58.92804035961495,"d":"58.93"},{"v":58.665641195648135,"d":"58.67"},{"v":58.22211979914286,"d":"58.22"},{"v":57.58800012007108,"d":"57.59"},{"v":56.74964150205397,"d":"56.75"},{"v":55.68889306298975,"d":"55.69"},{"v":54.3827079930633,"d":"54.38"},{"v":52.8027975888045,"d":"52.80"},{"v":50.91547110294917,"d":"50.92"},{"v":48.68191256645686,"d":"48.68"},{"v":46.05929666412984,"d":"46.06"},{"v":43.00332869995458,"d":"43.00"},{"v":39.47293991781649,"d":"39.47"},{"v":35.43780548044363,"d":"35.44"},{"v":30.88877569320852,"d":"30.89"},{"v":25.849911536808456,"d":"25.85"},{"v":20.38869871813815,"d":"20.39"},{"v":14.619297938370392,"d":"14.62"},{"v":8.849897158602623,"d":"8.85"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",105]
[null,"Declinacion . radianes",{"v":0.16432088762716554,"d":"0.164"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.7123894543671803,"d":"1.712"}]
[null,"Distancia sol - tierra. Bo",{"v":1.0329835806761896,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":0.9253109115404023,"d":"0.925"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":9981.84876433483,"d":"9,982"}]
[null,"H1",{"v":37304.27892273464,"d":"37,304"}]
[null,"H2",{"v":0.7437616492289333,"d":"0.744"}]
[null,"H3",{"v":0.18154926231146912,"d":"0.182"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":5758.305555555556,"d":"5,758"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.576877659790839,"d":"0.577"}]
[null,"Fraccion difusa diaria promedio",{"v":0.39146193761426384,"d":"0.391"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.7185926028086285,"d":"0.719"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.36667592950782857,"d":"0.367"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":8.849897158602623,"d":"8.85"},{"v":14.619297938370392,"d":"14.62"},{"v":20.38869871813815,"d":"20.39"},{"v":25.849911536808456,"d":"25.85"},{"v":30.88877569320852,"d":"30.89"},{"v":35.43780548044363,"d":"35.44"},{"v":39.47293991781649,"d":"39.47"},{"v":43.00332869995458,"d":"43.00"},{"v":46.05929666412984,"d":"46.06"},{"v":48.68191256645686,"d":"48.68"},{"v":50.91547110294917,"d":"50.92"},{"v":52.8027975888045,"d":"52.80"},{"v":54.3827079930633,"d":"54.38"},{"v":55.68889306298975,"d":"55.69"},{"v":56.74964150205397,"d":"56.75"},{"v":57.58800012007108,"d":"57.59"},{"v":58.22211979914286,"d":"58.22"},{"v":58.665641195648135,"d":"58.67"},{"v":58.92804035961495,"d":"58.93"},{"v":59.01489334688005,"d":"59.01"},{"v":58.92804035961495,"d":"58.93"},{"v":58.665641195648135,"d":"58.67"},{"v":58.22211979914286,"d":"58.22"},{"v":57.58800012007108,"d":"57.59"},{"v":56.74964150205397,"d":"56.75"},{"v":55.68889306298975,"d":"55.69"},{"v":54.3827079930633,"d":"54.38"},{"v":52.8027975888045,"d":"52.80"},{"v":50.91547110294917,"d":"50.92"},{"v":48.68191256645686,"d":"48.68"},{"v":46.05929666412984,"d":"46.06"},{"v":43.00332869995458,"d":"43.00"},{"v":39.47293991781649,"d":"39.47"},{"v":35.43780548044363,"d":"35.44"},{"v":30.88877569320852,"d":"30.89"},{"v":25.849911536808456,"d":"25.85"},{"v":20.38869871813815,"d":"20.39"},{"v":14.619297938370392,"d":"14.62"},{"v":8.849897158602623,"d":"8.85"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":98.1126886179493,"d":"98.11"},{"v":86.35016730968174,"d":"86.35"},{"v":78.76502369223323,"d":"78.77"},{"v":71.1795086202555,"d":"71.18"},{"v":63.94443672791597,"d":"63.94"},{"v":57.16574158165265,"d":"57.17"},{"v":50.90160450511881,"d":"50.90"},{"v":45.16613164344728,"d":"45.17"},{"v":39.939944007590434,"d":"39.94"},{"v":35.18245421674971,"d":"35.18"},{"v":30.842388880103595,"d":"30.84"},{"v":26.86527325448092,"d":"26.87"},{"v":23.198005582366108,"d":"23.20"},{"v":19.791219328152447,"d":"19.79"},{"v":16.60018411290075,"d":"16.60"},{"v":13.584839271652314,"d":"13.58"},{"v":10.709363002077406,"d":"10.71"},{"v":7.941523630218584,"d":"7.94"},{"v":5.251950644270247,"d":"5.25"},{"v":2.613394108644276,"d":"2.61"},{"v":0,"d":"0.00"},{"v":-2.613394108644276,"d":"-2.61"},{"v":-5.251950644270247,"d":"-5.25"},{"v":-7.941523630218584,"d":"-7.94"},{"v":-10.709363002077406,"d":"-10.71"},{"v":-13.584839271652314,"d":"-13.58"},{"v":-16.60018411290075,"d":"-16.60"},{"v":-19.791219328152447,"d":"-19.79"},{"v":-23.198005582366108,"d":"-23.20"},{"v":-26.86527325448092,"d":"-26.87"},{"v":-30.842388880103595,"d":"-30.84"},{"v":-35.18245421674971,"d":"-35.18"},{"v":-39.939944007590434,"d":"-39.94"},{"v":-45.16613164344728,"d":"-45.17"},{"v":-50.90160450511881,"d":"-50.90"},{"v":-57.16574158165265,"d":"-57.17"},{"v":-63.94443672791597,"d":"-63.94"},{"v":-71.1795086202555,"d":"-71.18"},{"v":-78.76502369223323,"d":"-78.77"},{"v":-86.35016730968174,"d":"-86.35"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"},{"v":-98.1126886179493,"d":"-98.11"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-1.4922045154123438,"d":"-1.49"},{"v":-1.4038513614427135,"d":"-1.40"},{"v":-1.3575504403172198,"d":"-1.36"},{"v":-1.3267402647004416,"d":"-1.33"},{"v":-1.303293176922595,"d":"-1.30"},{"v":-1.284114329289706,"d":"-1.28"},{"v":-1.2677494831482947,"d":"-1.27"},{"v":-1.253400140129266,"d":"-1.25"},{"v":-1.24056949305908,"d":"-1.24"},{"v":-1.2289164174449498,"d":"-1.23"},{"v":-1.2181886731045943,"d":"-1.22"},{"v":-1.2081893117949736,"d":"-1.21"},{"v":-1.1987580676651366,"d":"-1.20"},{"v":-1.1897599693855707,"d":"-1.19"},{"v":-1.1810776611005478,"d":"-1.18"},{"v":-1.1726057338488487,"d":"-1.17"},{"v":-1.1642461724735995,"d":"-1.16"},{"v":-1.1559043862000602,"d":"-1.16"},{"v":-1.147485451693646,"d":"-1.15"},{"v":-1.138890255420306,"d":"-1.14"},{"v":-1.1300112172699794,"d":"-1.13"},{"v":-1.1207272204363778,"d":"-1.12"},{"v":-1.1108972565709756,"d":"-1.11"},{"v":-1.1003520971027705,"d":"-1.10"},{"v":-1.0888829761952175,"d":"-1.09"},{"v":-1.0762257363019088,"d":"-1.08"},{"v":-1.0620379948914715,"d":"-1.06"},{"v":-1.0458653624065481,"d":"-1.05"},{"v":-1.0270900360137096,"d":"-1.03"},{"v":-1.0048501087605997,"d":"-1.00"},{"v":-0.9779082939046257,"d":"-0.98"},{"v":-0.9444290089038152,"d":"-0.94"},{"v":-0.9015793610522751,"d":"-0.90"},{"v":-0.8447658878346214,"d":"-0.84"},{"v":-0.7660444431189781,"d":"-0.77"},{"v":-0.650413233563192,"d":"-0.65"},{"v":-0.46572897779642314,"d":"-0.47"},{"v":-0.12823752479524225,"d":"-0.13"},{"v":0.6370853696056067,"d":"0.64"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1.4922045154123438,"d":"1.49"},{"v":1.4038513614427135,"d":"1.40"},{"v":1.3575504403172198,"d":"1.36"},{"v":1.3267402647004416,"d":"1.33"},{"v":1.303293176922595,"d":"1.30"},{"v":1.284114329289706,"d":"1.28"},{"v":1.2677494831482947,"d":"1.27"},{"v":1.253400140129266,"d":"1.25"},{"v":1.24056949305908,"d":"1.24"},{"v":1.2289164174449498,"d":"1.23"},{"v":1.2181886731045943,"d":"1.22"},{"v":1.2081893117949736,"d":"1.21"},{"v":1.1987580676651366,"d":"1.20"},{"v":1.1897599693855707,"d":"1.19"},{"v":1.1810776611005478,"d":"1.18"},{"v":1.1726057338488487,"d":"1.17"},{"v":1.1642461724735995,"d":"1.16"},{"v":1.1559043862000602,"d":"1.16"},{"v":1.147485451693646,"d":"1.15"},{"v":1.138890255420306,"d":"1.14"},{"v":1.1300112172699794,"d":"1.13"},{"v":1.1207272204363778,"d":"1.12"},{"v":1.1108972565709756,"d":"1.11"},{"v":1.1003520971027705,"d":"1.10"},{"v":1.0888829761952175,"d":"1.09"},{"v":1.0762257363019088,"d":"1.08"},{"v":1.0620379948914715,"d":"1.06"},{"v":1.0458653624065481,"d":"1.05"},{"v":1.0270900360137096,"d":"1.03"},{"v":1.0048501087605997,"d":"1.00"},{"v":0.9779082939046257,"d":"0.98"},{"v":0.9444290089038152,"d":"0.94"},{"v":0.9015793610522751,"d":"0.90"},{"v":0.8447658878346214,"d":"0.84"},{"v":0.7660444431189781,"d":"0.77"},{"v":0.650413233563192,"d":"0.65"},{"v":0.46572897779642314,"d":"0.47"},{"v":0.12823752479524225,"d":"0.13"},{"v":0.6370853696056067,"d":"0.64"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":92.98194711709367,"d":"92.98"},{"v":162.4322425115519,"d":"162.43"},{"v":237.50511622267422,"d":"237.51"},{"v":312.4340325080602,"d":"312.43"},{"v":383.655499122177,"d":"383.66"},{"v":448.6293477262566,"d":"448.63"},{"v":506.00474555443384,"d":"506.00"},{"v":555.4418149813744,"d":"555.44"},{"v":597.2862870382914,"d":"597.29"},{"v":632.2545575511772,"d":"632.25"},{"v":661.200459637277,"d":"661.20"},{"v":684.9714233634272,"d":"684.97"},{"v":704.3338338624793,"d":"704.33"},{"v":719.9429247321975,"d":"719.94"},{"v":732.3375915428477,"d":"732.34"},{"v":741.9471843592196,"d":"741.95"},{"v":749.102682739673,"d":"749.10"},{"v":754.0481870879951,"d":"754.05"},{"v":756.9507405307539,"d":"756.95"},{"v":757.9076149736665,"d":"757.91"},{"v":756.9507405307539,"d":"756.95"},{"v":754.0481870879951,"d":"754.05"},{"v":749.102682739673,"d":"749.10"},{"v":741.9471843592196,"d":"741.95"},{"v":732.3375915428477,"d":"732.34"},{"v":719.9429247321975,"d":"719.94"},{"v":704.3338338624793,"d":"704.33"},{"v":684.9714233634272,"d":"684.97"},{"v":661.200459637277,"d":"661.20"},{"v":632.2545575511772,"d":"632.25"},{"v":597.2862870382914,"d":"597.29"},{"v":555.4418149813744,"d":"555.44"},{"v":506.00474555443384,"d":"506.00"},{"v":448.6293477262566,"d":"448.63"},{"v":383.655499122177,"d":"383.66"},{"v":312.4340325080602,"d":"312.43"},{"v":237.50511622267422,"d":"237.51"},{"v":162.4322425115519,"d":"162.43"},{"v":92.98194711709367,"d":"92.98"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":49.05943282245731,"d":"49.06"},{"v":80.48527366735892,"d":"80.49"},{"v":111.09572412603465,"d":"111.10"},{"v":139.03906706185882,"d":"139.04"},{"v":163.7074119894643,"d":"163.71"},{"v":184.89601748637904,"d":"184.90"},{"v":202.72008522749186,"d":"202.72"},{"v":217.49314884658497,"d":"217.49"},{"v":229.6163850630143,"d":"229.62"},{"v":239.50101961398863,"d":"239.50"},{"v":247.52448370213835,"d":"247.52"},{"v":254.0115021744585,"d":"254.01"},{"v":259.2302597860986,"d":"259.23"},{"v":263.39618404830554,"d":"263.40"},{"v":266.6786948380718,"d":"266.68"},{"v":269.20840310106075,"d":"269.21"},{"v":271.0835738480618,"d":"271.08"},{"v":272.37540141692205,"d":"272.38"},{"v":273.13200182656635,"d":"273.13"},{"v":273.3811721758127,"d":"273.38"},{"v":273.13200182656635,"d":"273.13"},{"v":272.37540141692205,"d":"272.38"},{"v":271.0835738480618,"d":"271.08"},{"v":269.20840310106075,"d":"269.21"},{"v":266.6786948380718,"d":"266.68"},{"v":263.39618404830554,"d":"263.40"},{"v":259.2302597860986,"d":"259.23"},{"v":254.0115021744585,"d":"254.01"},{"v":247.52448370213835,"d":"247.52"},{"v":239.50101961398863,"d":"239.50"},{"v":229.6163850630143,"d":"229.62"},{"v":217.49314884658497,"d":"217.49"},{"v":202.72008522749186,"d":"202.72"},{"v":184.89601748637904,"d":"184.90"},{"v":163.7074119894643,"d":"163.71"},{"v":139.03906706185882,"d":"139.04"},{"v":111.09572412603465,"d":"111.10"},{"v":80.48527366735892,"d":"80.49"},{"v":49.05943282245731,"d":"49.06"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":286.6568412372409,"d":"286.66"},{"v":338.6637484723209,"d":"338.66"},{"v":384.4889713762868,"d":"384.49"},{"v":423.58490548984355,"d":"423.58"},{"v":456.12006390655125,"d":"456.12"},{"v":482.6612707805989,"d":"482.66"},{"v":503.9353882196747,"d":"503.94"},{"v":520.6811705925161,"d":"520.68"},{"v":533.5715003706481,"d":"533.57"},{"v":543.1810362191494,"d":"543.18"},{"v":549.9793205907383,"d":"549.98"},{"v":554.3362055160337,"d":"554.34"},{"v":556.5319178962991,"d":"556.53"},{"v":556.7676856703948,"d":"556.77"},{"v":555.1749639198247,"d":"555.17"},{"v":551.82244419594,"d":"551.82"},{"v":546.7206018611452,"d":"546.72"},{"v":539.8238022449889,"d":"539.82"},{"v":531.0301166561934,"d":"531.03"},{"v":520.1791093392229,"d":"520.18"},{"v":507.0480453356777,"d":"507.05"},{"v":491.34735214875826,"d":"491.35"},{"v":472.71690733110694,"d":"472.72"},{"v":450.72605415699815,"d":"450.73"},{"v":424.88247302122807,"d":"424.88"},{"v":394.6584353122942,"d":"394.66"},{"v":359.5474465607243,"d":"359.55"},{"v":319.16852381804546,"d":"319.17"},{"v":273.43519027452066,"d":"273.44"},{"v":222.79292087167156,"d":"222.79"},{"v":168.49000992266338,"d":"168.49"},{"v":112.77838015944181,"d":"112.78"},{"v":58.872516965035196,"d":"58.87"},{"v":10.50867644905214,"d":"10.51"},{"v":27.982391253405947,"d":"27.98"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":144.5572826206913,"d":"144.56"},{"v":163.26729211832452,"d":"163.27"},{"v":179.0063400123088,"d":"179.01"},{"v":192.05128346848005,"d":"192.05"},{"v":202.75637044480195,"d":"202.76"},{"v":211.48472240530697,"d":"211.48"},{"v":218.56961948902773,"d":"218.57"},{"v":224.29780095175332,"d":"224.30"},{"v":228.90607989176425,"d":"228.91"},{"v":232.58468358862677,"d":"232.58"},{"v":235.4832135584992,"d":"235.48"},{"v":237.71700216878108,"d":"237.72"},{"v":239.37281960760131,"d":"239.37"},{"v":240.5135320573281,"d":"240.51"},{"v":241.181627031885,"d":"241.18"},{"v":241.4016499872233,"d":"241.40"},{"v":241.181627031885,"d":"241.18"},{"v":240.5135320573281,"d":"240.51"},{"v":239.37281960760131,"d":"239.37"},{"v":237.71700216878108,"d":"237.72"},{"v":235.4832135584992,"d":"235.48"},{"v":232.58468358862677,"d":"232.58"},{"v":228.90607989176425,"d":"228.91"},{"v":224.29780095175332,"d":"224.30"},{"v":218.56961948902773,"d":"218.57"},{"v":211.48472240530697,"d":"211.48"},{"v":202.75637044480195,"d":"202.76"},{"v":192.05128346848005,"d":"192.05"},{"v":179.0063400123088,"d":"179.01"},{"v":163.26729211832452,"d":"163.27"},{"v":144.5572826206913,"d":"144.56"},{"v":122.77458588052134,"d":"122.77"},{"v":98.09999312353123,"d":"98.10"},{"v":71.07028515657471,"d":"71.07"},{"v":43.32056935933476,"d":"43.32"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":431.2141238579322,"d":"431.21"},{"v":501.9310405906454,"d":"501.93"},{"v":563.4953113885956,"d":"563.50"},{"v":615.6361889583236,"d":"615.64"},{"v":658.8764343513532,"d":"658.88"},{"v":694.1459931859058,"d":"694.15"},{"v":722.5050077087024,"d":"722.51"},{"v":744.9789715442694,"d":"744.98"},{"v":762.4775802624124,"d":"762.48"},{"v":775.7657198077761,"d":"775.77"},{"v":785.4625341492375,"d":"785.46"},{"v":792.0532076848148,"d":"792.05"},{"v":795.9047375039004,"d":"795.90"},{"v":797.281217727723,"d":"797.28"},{"v":796.3565909517097,"d":"796.36"},{"v":793.2240941831633,"d":"793.22"},{"v":787.9022288930302,"d":"787.90"},{"v":780.337334302317,"d":"780.34"},{"v":770.4029362637947,"d":"770.40"},{"v":757.896111508004,"d":"757.90"},{"v":742.531258894177,"d":"742.53"},{"v":723.932035737385,"d":"723.93"},{"v":701.6229872228712,"d":"701.62"},{"v":675.0238551087515,"d":"675.02"},{"v":643.4520925102559,"d":"643.45"},{"v":606.1431577176012,"d":"606.14"},{"v":562.3038170055263,"d":"562.30"},{"v":511.2198072865255,"d":"511.22"},{"v":452.44153028682945,"d":"452.44"},{"v":386.0602129899961,"d":"386.06"},{"v":313.0472925433547,"d":"313.05"},{"v":235.55296603996317,"d":"235.55"},{"v":156.97251008856642,"d":"156.97"},{"v":81.57896160562686,"d":"81.58"},{"v":71.3029606127407,"d":"71.30"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":286.6568412372409,"d":"286.66"},{"v":338.6637484723209,"d":"338.66"},{"v":384.4889713762868,"d":"384.49"},{"v":423.58490548984355,"d":"423.58"},{"v":456.12006390655125,"d":"456.12"},{"v":482.6612707805989,"d":"482.66"},{"v":503.9353882196747,"d":"503.94"},{"v":520.6811705925161,"d":"520.68"},{"v":533.5715003706481,"d":"533.57"},{"v":543.1810362191494,"d":"543.18"},{"v":549.9793205907383,"d":"549.98"},{"v":554.3362055160337,"d":"554.34"},{"v":556.5319178962991,"d":"556.53"},{"v":556.7676856703948,"d":"556.77"},{"v":555.1749639198247,"d":"555.17"},{"v":551.82244419594,"d":"551.82"},{"v":546.7206018611452,"d":"546.72"},{"v":539.8238022449889,"d":"539.82"},{"v":531.0301166561934,"d":"531.03"},{"v":520.1791093392229,"d":"520.18"},{"v":507.0480453356777,"d":"507.05"},{"v":491.34735214875826,"d":"491.35"},{"v":472.71690733110694,"d":"472.72"},{"v":450.72605415699815,"d":"450.73"},{"v":424.88247302122807,"d":"424.88"},{"v":394.6584353122942,"d":"394.66"},{"v":359.5474465607243,"d":"359.55"},{"v":319.16852381804546,"d":"319.17"},{"v":273.43519027452066,"d":"273.44"},{"v":222.79292087167156,"d":"222.79"},{"v":168.49000992266338,"d":"168.49"},{"v":112.77838015944181,"d":"112.78"},{"v":58.872516965035196,"d":"58.87"},{"v":10.50867644905214,"d":"10.51"},{"v":27.982391253405947,"d":"27.98"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":431.2141238579322,"d":"431.21"},{"v":501.9310405906454,"d":"501.93"},{"v":563.4953113885956,"d":"563.50"},{"v":615.6361889583236,"d":"615.64"},{"v":658.8764343513532,"d":"658.88"},{"v":694.1459931859058,"d":"694.15"},{"v":722.5050077087024,"d":"722.51"},{"v":744.9789715442694,"d":"744.98"},{"v":762.4775802624124,"d":"762.48"},{"v":775.7657198077761,"d":"775.77"},{"v":785.4625341492375,"d":"785.46"},{"v":792.0532076848148,"d":"792.05"},{"v":795.9047375039004,"d":"795.90"},{"v":797.281217727723,"d":"797.28"},{"v":796.3565909517097,"d":"796.36"},{"v":793.2240941831633,"d":"793.22"},{"v":787.9022288930302,"d":"787.90"},{"v":780.337334302317,"d":"780.34"},{"v":770.4029362637947,"d":"770.40"},{"v":757.896111508004,"d":"757.90"},{"v":742.531258894177,"d":"742.53"},{"v":723.932035737385,"d":"723.93"},{"v":701.6229872228712,"d":"701.62"},{"v":675.0238551087515,"d":"675.02"},{"v":643.4520925102559,"d":"643.45"},{"v":606.1431577176012,"d":"606.14"},{"v":562.3038170055263,"d":"562.30"},{"v":511.2198072865255,"d":"511.22"},{"v":452.44153028682945,"d":"452.44"},{"v":386.0602129899961,"d":"386.06"},{"v":313.0472925433547,"d":"313.05"},{"v":235.55296603996317,"d":"235.55"},{"v":156.97251008856642,"d":"156.97"},{"v":81.57896160562686,"d":"81.58"},{"v":71.3029606127407,"d":"71.30"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":14230.866388136234,"d":"14,231"},"W/m2"]
[null,"Total Directa disponible",{"v":14230.866388136234,"d":"14,231"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":21191.032810473782,"d":"21,191"}]
[null,"Total global ",{"v":21191.032810473782,"d":"21,191"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.328448664328312,"d":"0.328"},{"v":0.39146193761426384,"d":"0.391"}]
[]
[null,"MAYO"]
[null,"Declinacion dia tipo",{"v":18.91195474122616,"d":"18.91"},{"v":0.3300758782225487,"d":"0.33"}]
[null,"ocaso",{"v":-106.95279169277775,"d":"-106.95"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"},{"v":-0.42013051909052584,"d":"-0.420"}]
[null,"c",{"v":-0.4748901828294522,"d":"-0.475"},{"v":-0.47048488245947534,"d":"-0.470"},{"v":-0.45740283417209654,"d":"-0.457"},{"v":-0.43604152938469226,"d":"-0.436"},{"v":-0.407050020533886,"d":"-0.407"},{"v":-0.37130919994569817,"d":"-0.371"},{"v":-0.3299050343679729,"d":"-0.330"},{"v":-0.28409556842027034,"d":"-0.284"},{"v":-0.2352726995447038,"d":"-0.235"},{"v":-0.18491988590649344,"d":"-0.185"},{"v":-0.13456707226828302,"d":"-0.135"},{"v":-0.08574420339271628,"d":"-0.086"},{"v":-0.03993473744501401,"d":"-0.040"},{"v":0.0014694281327112535,"d":"0.001"},{"v":0.03721024872089912,"d":"0.037"},{"v":0.06620175757170536,"d":"0.066"},{"v":0.0875630623591096,"d":"0.088"},{"v":0.10064511064648825,"d":"0.101"},{"v":0.10505041101646521,"d":"0.105"},{"v":0.10064511064648826,"d":"0.101"},{"v":0.08756306235910959,"d":"0.088"},{"v":0.0662017575717054,"d":"0.066"},{"v":0.03721024872089908,"d":"0.037"},{"v":0.001469428132711198,"d":"0.001"},{"v":-0.039934737445014204,"d":"-0.040"},{"v":-0.0857442033927165,"d":"-0.086"},{"v":-0.13456707226828302,"d":"-0.135"},{"v":-0.18491988590649355,"d":"-0.185"},{"v":-0.23527269954470398,"d":"-0.235"},{"v":-0.28409556842027056,"d":"-0.284"},{"v":-0.3299050343679729,"d":"-0.330"},{"v":-0.37130919994569817,"d":"-0.371"},{"v":-0.4070500205338861,"d":"-0.407"},{"v":-0.4360415293846925,"d":"-0.436"},{"v":-0.45740283417209654,"d":"-0.457"},{"v":-0.47048488245947534,"d":"-0.470"},{"v":-0.4748901828294522,"d":"-0.475"},{"v":-0.47048488245947534,"d":"-0.470"},{"v":-0.45740283417209654,"d":"-0.457"},{"v":-0.4360415293846925,"d":"-0.436"},{"v":-0.4070500205338861,"d":"-0.407"},{"v":-0.37130919994569817,"d":"-0.371"},{"v":-0.3299050343679729,"d":"-0.330"},{"v":-0.28409556842027056,"d":"-0.284"},{"v":-0.23527269954470398,"d":"-0.235"},{"v":-0.18491988590649355,"d":"-0.185"},{"v":-0.13456707226828302,"d":"-0.135"},{"v":-0.0857442033927165,"d":"-0.086"},{"v":-0.039934737445014204,"d":"-0.040"},{"v":0.001469428132711198,"d":"0.001"},{"v":0.03721024872089908,"d":"0.037"},{"v":0.0662017575717054,"d":"0.066"},{"v":0.08756306235910959,"d":"0.088"},{"v":0.10064511064648826,"d":"0.101"},{"v":0.10505041101646521,"d":"0.105"},{"v":0.10064511064648825,"d":"0.101"},{"v":0.0875630623591096,"d":"0.088"},{"v":0.06620175757170536,"d":"0.066"},{"v":0.03721024872089912,"d":"0.037"},{"v":0.0014694281327112535,"d":"0.001"},{"v":-0.03993473744501401,"d":"-0.040"},{"v":-0.08574420339271628,"d":"-0.086"},{"v":-0.13456707226828302,"d":"-0.135"},{"v":-0.18491988590649344,"d":"-0.185"},{"v":-0.2352726995447038,"d":"-0.235"},{"v":-0.28409556842027034,"d":"-0.284"},{"v":-0.3299050343679729,"d":"-0.330"},{"v":-0.37130919994569817,"d":"-0.371"},{"v":-0.407050020533886,"d":"-0.407"},{"v":-0.43604152938469226,"d":"-0.436"},{"v":-0.45740283417209654,"d":"-0.457"},{"v":-0.47048488245947534,"d":"-0.470"},{"v":-0.4748901828294522,"d":"-0.475"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":14.51190858412859,"d":"14.51"},{"v":19.13921262899882,"d":"19.14"},{"v":24.33045404578042,"d":"24.33"},{"v":30.005600311167623,"d":"30.01"},{"v":35.68074657655481,"d":"35.68"},{"v":40.87198799333643,"d":"40.87"},{"v":45.499292038206654,"d":"45.50"},{"v":49.54043508389371,"d":"49.54"},{"v":53.016947719625804,"d":"53.02"},{"v":55.97655242525198,"d":"55.98"},{"v":58.478193891854154,"d":"58.48"},{"v":60.58190500334234,"d":"60.58"},{"v":62.343150092978874,"d":"62.34"},{"v":63.810335990666594,"d":"63.81"},{"v":65.02420906151745,"d":"65.02"},{"v":66.01821448419915,"d":"66.02"},{"v":66.81925160956291,"d":"66.82"},{"v":67.44851621409688,"d":"67.45"},{"v":67.92227827981243,"d":"67.92"},{"v":68.25253124163979,"d":"68.25"},{"v":68.44749254842992,"d":"68.45"},{"v":68.51195474122618,"d":"68.51"},{"v":68.44749254842992,"d":"68.45"},{"v":68.25253124163979,"d":"68.25"},{"v":67.92227827981243,"d":"67.92"},{"v":67.44851621409688,"d":"67.45"},{"v":66.81925160956291,"d":"66.82"},{"v":66.01821448419915,"d":"66.02"},{"v":65.02420906151745,"d":"65.02"},{"v":63.810335990666594,"d":"63.81"},{"v":62.343150092978874,"d":"62.34"},{"v":60.58190500334234,"d":"60.58"},{"v":58.478193891854154,"d":"58.48"},{"v":55.97655242525198,"d":"55.98"},{"v":53.016947719625804,"d":"53.02"},{"v":49.54043508389371,"d":"49.54"},{"v":45.499292038206654,"d":"45.50"},{"v":40.87198799333643,"d":"40.87"},{"v":35.68074657655481,"d":"35.68"},{"v":30.005600311167623,"d":"30.01"},{"v":24.33045404578042,"d":"24.33"},{"v":19.13921262899882,"d":"19.14"},{"v":14.51190858412859,"d":"14.51"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",135.5]
[null,"Declinacion . radianes",{"v":0.3300758782225487,"d":"0.330"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.8666783592386114,"d":"1.867"}]
[null,"Distancia sol - tierra. Bo",{"v":1.0329726579359546,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":1.0812470372710836,"d":"1.081"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":11663.896043023355,"d":"11,664"}]
[null,"H1",{"v":36738.94089858006,"d":"36,739"}]
[null,"H2",{"v":0.6891227632500991,"d":"0.689"}]
[null,"H3",{"v":0.39212427402098443,"d":"0.392"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":6609.533333333333,"d":"6,610"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.5666660015618675,"d":"0.567"}]
[null,"Fraccion difusa diaria promedio",{"v":0.4201081683645567,"d":"0.420"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.7755650301611348,"d":"0.776"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.3125316788719838,"d":"0.313"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":14.51190858412859,"d":"14.51"},{"v":19.13921262899882,"d":"19.14"},{"v":24.33045404578042,"d":"24.33"},{"v":30.005600311167623,"d":"30.01"},{"v":35.68074657655481,"d":"35.68"},{"v":40.87198799333643,"d":"40.87"},{"v":45.499292038206654,"d":"45.50"},{"v":49.54043508389371,"d":"49.54"},{"v":53.016947719625804,"d":"53.02"},{"v":55.97655242525198,"d":"55.98"},{"v":58.478193891854154,"d":"58.48"},{"v":60.58190500334234,"d":"60.58"},{"v":62.343150092978874,"d":"62.34"},{"v":63.810335990666594,"d":"63.81"},{"v":65.02420906151745,"d":"65.02"},{"v":66.01821448419915,"d":"66.02"},{"v":66.81925160956291,"d":"66.82"},{"v":67.44851621409688,"d":"67.45"},{"v":67.92227827981243,"d":"67.92"},{"v":68.25253124163979,"d":"68.25"},{"v":68.44749254842992,"d":"68.45"},{"v":68.51195474122618,"d":"68.51"},{"v":68.44749254842992,"d":"68.45"},{"v":68.25253124163979,"d":"68.25"},{"v":67.92227827981243,"d":"67.92"},{"v":67.44851621409688,"d":"67.45"},{"v":66.81925160956291,"d":"66.82"},{"v":66.01821448419915,"d":"66.02"},{"v":65.02420906151745,"d":"65.02"},{"v":63.810335990666594,"d":"63.81"},{"v":62.343150092978874,"d":"62.34"},{"v":60.58190500334234,"d":"60.58"},{"v":58.478193891854154,"d":"58.48"},{"v":55.97655242525198,"d":"55.98"},{"v":53.016947719625804,"d":"53.02"},{"v":49.54043508389371,"d":"49.54"},{"v":45.499292038206654,"d":"45.50"},{"v":40.87198799333643,"d":"40.87"},{"v":35.68074657655481,"d":"35.68"},{"v":30.005600311167623,"d":"30.01"},{"v":24.33045404578042,"d":"24.33"},{"v":19.13921262899882,"d":"19.14"},{"v":14.51190858412859,"d":"14.51"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":106.95279169277777,"d":"106.95"},{"v":86.7760599956041,"d":"86.78"},{"v":80.58915295495058,"d":"80.59"},{"v":73.72211390282519,"d":"73.72"},{"v":66.26137417651034,"d":"66.26"},{"v":58.799862891847454,"d":"58.80"},{"v":51.922680263841826,"d":"51.92"},{"v":45.6979917546622,"d":"45.70"},{"v":40.133637208682664,"d":"40.13"},{"v":35.1926118961171,"d":"35.19"},{"v":30.811803963506506,"d":"30.81"},{"v":26.917678507872253,"d":"26.92"},{"v":23.436689941162623,"d":"23.44"},{"v":20.300909577400102,"d":"20.30"},{"v":17.45030944844402,"d":"17.45"},{"v":14.833077518913308,"d":"14.83"},{"v":12.40494054568621,"d":"12.40"},{"v":10.128083283359658,"d":"10.13"},{"v":7.96997729996236,"d":"7.97"},{"v":5.902264417691646,"d":"5.90"},{"v":3.8997466054958583,"d":"3.90"},{"v":1.9394864721823335,"d":"1.94"},{"v":0,"d":"0.00"},{"v":-1.9394864721823335,"d":"-1.94"},{"v":-3.8997466054958583,"d":"-3.90"},{"v":-5.902264417691646,"d":"-5.90"},{"v":-7.96997729996236,"d":"-7.97"},{"v":-10.128083283359658,"d":"-10.13"},{"v":-12.40494054568621,"d":"-12.40"},{"v":-14.833077518913308,"d":"-14.83"},{"v":-17.45030944844402,"d":"-17.45"},{"v":-20.300909577400102,"d":"-20.30"},{"v":-23.436689941162623,"d":"-23.44"},{"v":-26.917678507872253,"d":"-26.92"},{"v":-30.811803963506506,"d":"-30.81"},{"v":-35.1926118961171,"d":"-35.19"},{"v":-40.133637208682664,"d":"-40.13"},{"v":-45.6979917546622,"d":"-45.70"},{"v":-51.922680263841826,"d":"-51.92"},{"v":-58.799862891847454,"d":"-58.80"},{"v":-66.26137417651034,"d":"-66.26"},{"v":-73.72211390282519,"d":"-73.72"},{"v":-80.58915295495058,"d":"-80.59"},{"v":-86.7760599956041,"d":"-86.78"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"},{"v":-106.95279169277777,"d":"-106.95"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-0.8669878599998876,"d":"-0.87"},{"v":-0.9620492928474823,"d":"-0.96"},{"v":-1.0197587925428597,"d":"-1.02"},{"v":-1.054133211558963,"d":"-1.05"},{"v":-1.072210010632158,"d":"-1.07"},{"v":-1.0799601341820488,"d":"-1.08"},{"v":-1.081885061831902,"d":"-1.08"},{"v":-1.0804838750425423,"d":"-1.08"},{"v":-1.077203253448157,"d":"-1.08"},{"v":-1.0728924087569773,"d":"-1.07"},{"v":-1.0680477646161701,"d":"-1.07"},{"v":-1.062954054320012,"d":"-1.06"},{"v":-1.0577683563907232,"d":"-1.06"},{"v":-1.0525706549669527,"d":"-1.05"},{"v":-1.047394237898834,"d":"-1.05"},{"v":-1.0422438493348134,"d":"-1.04"},{"v":-1.0371063798076279,"d":"-1.04"},{"v":-1.0319569802557715,"d":"-1.03"},{"v":-1.0267623264814543,"d":"-1.03"},{"v":-1.0214820490903542,"d":"-1.02"},{"v":-1.016068903377121,"d":"-1.02"},{"v":-1.0104679726176675,"d":"-1.01"},{"v":-1.0046150063603143,"d":"-1.00"},{"v":-0.998433846352418,"d":"-1.00"},{"v":-0.9918327533317909,"d":"-0.99"},{"v":-0.9846992892197711,"d":"-0.98"},{"v":-0.9768931998497086,"d":"-0.98"},{"v":-0.9682364414893246,"d":"-0.97"},{"v":-0.9584990373894854,"d":"-0.96"},{"v":-0.94737873800602,"d":"-0.95"},{"v":-0.9344713229754713,"d":"-0.93"},{"v":-0.9192265350818952,"d":"-0.92"},{"v":-0.900881553721522,"d":"-0.90"},{"v":-0.8783585936420604,"d":"-0.88"},{"v":-0.850103562436821,"d":"-0.85"},{"v":-0.813823955144952,"d":"-0.81"},{"v":-0.7660444431189779,"d":"-0.77"},{"v":-0.7013062202554972,"d":"-0.70"},{"v":-0.6106001106709859,"d":"-0.61"},{"v":-0.47795567467899347,"d":"-0.48"},{"v":-0.2863784751846114,"d":"-0.29"},{"v":-0.0149101078389018,"d":"-0.01"},{"v":0.3871827134914322,"d":"0.39"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.8669878599998876,"d":"0.87"},{"v":0.9620492928474823,"d":"0.96"},{"v":1.0197587925428597,"d":"1.02"},{"v":1.054133211558963,"d":"1.05"},{"v":1.072210010632158,"d":"1.07"},{"v":1.0799601341820488,"d":"1.08"},{"v":1.081885061831902,"d":"1.08"},{"v":1.0804838750425423,"d":"1.08"},{"v":1.077203253448157,"d":"1.08"},{"v":1.0728924087569773,"d":"1.07"},{"v":1.0680477646161701,"d":"1.07"},{"v":1.062954054320012,"d":"1.06"},{"v":1.0577683563907232,"d":"1.06"},{"v":1.0525706549669527,"d":"1.05"},{"v":1.047394237898834,"d":"1.05"},{"v":1.0422438493348134,"d":"1.04"},{"v":1.0371063798076279,"d":"1.04"},{"v":1.0319569802557715,"d":"1.03"},{"v":1.0267623264814543,"d":"1.03"},{"v":1.0214820490903542,"d":"1.02"},{"v":1.016068903377121,"d":"1.02"},{"v":1.0104679726176675,"d":"1.01"},{"v":1.0046150063603143,"d":"1.00"},{"v":0.998433846352418,"d":"1.00"},{"v":0.9918327533317909,"d":"0.99"},{"v":0.9846992892197711,"d":"0.98"},{"v":0.9768931998497086,"d":"0.98"},{"v":0.9682364414893246,"d":"0.97"},{"v":0.9584990373894854,"d":"0.96"},{"v":0.94737873800602,"d":"0.95"},{"v":0.9344713229754713,"d":"0.93"},{"v":0.9192265350818952,"d":"0.92"},{"v":0.900881553721522,"d":"0.90"},{"v":0.8783585936420604,"d":"0.88"},{"v":0.850103562436821,"d":"0.85"},{"v":0.813823955144952,"d":"0.81"},{"v":0.7660444431189779,"d":"0.77"},{"v":0.7013062202554972,"d":"0.70"},{"v":0.6106001106709859,"d":"0.61"},{"v":0.47795567467899347,"d":"0.48"},{"v":0.2863784751846114,"d":"0.29"},{"v":0.0149101078389018,"d":"0.01"},{"v":0.3871827134914322,"d":"0.39"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":159.03167760721658,"d":"159.03"},{"v":216.87527092630492,"d":"216.88"},{"v":284.560717327442,"d":"284.56"},{"v":360.6912587677024,"d":"360.69"},{"v":437.5303330880656,"d":"437.53"},{"v":507.0181446364074,"d":"507.02"},{"v":567.2075725939802,"d":"567.21"},{"v":617.657171886784,"d":"617.66"},{"v":658.9868161359489,"d":"658.99"},{"v":692.3611942550319,"d":"692.36"},{"v":719.0961216580608,"d":"719.10"},{"v":740.4306442704903,"d":"740.43"},{"v":757.4282098958093,"d":"757.43"},{"v":770.9546697301829,"d":"770.95"},{"v":781.693119940078,"d":"781.69"},{"v":790.1718390610223,"d":"790.17"},{"v":796.7934896651734,"d":"796.79"},{"v":801.8606876340937,"d":"801.86"},{"v":805.5965184369301,"d":"805.60"},{"v":808.1600854215964,"d":"808.16"},{"v":809.6576860340483,"d":"809.66"},{"v":810.1502679080029,"d":"810.15"},{"v":809.6576860340483,"d":"809.66"},{"v":808.1600854215964,"d":"808.16"},{"v":805.5965184369301,"d":"805.60"},{"v":801.8606876340937,"d":"801.86"},{"v":796.7934896651734,"d":"796.79"},{"v":790.1718390610223,"d":"790.17"},{"v":781.693119940078,"d":"781.69"},{"v":770.9546697301829,"d":"770.95"},{"v":757.4282098958093,"d":"757.43"},{"v":740.4306442704903,"d":"740.43"},{"v":719.0961216580608,"d":"719.10"},{"v":692.3611942550319,"d":"692.36"},{"v":658.9868161359489,"d":"658.99"},{"v":617.657171886784,"d":"617.66"},{"v":567.2075725939802,"d":"567.21"},{"v":507.0181446364074,"d":"507.02"},{"v":437.5303330880656,"d":"437.53"},{"v":360.6912587677024,"d":"360.69"},{"v":284.560717327442,"d":"284.56"},{"v":216.87527092630492,"d":"216.88"},{"v":159.03167760721658,"d":"159.03"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"},{"v":-8.760896370911729e-14,"d":"-0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":84.23530387166129,"d":"84.24"},{"v":110.21483777371031,"d":"110.21"},{"v":138.49736270202183,"d":"138.50"},{"v":168.10829538810765,"d":"168.11"},{"v":196.07128236328586,"d":"196.07"},{"v":219.9732132617995,"d":"219.97"},{"v":239.76313240486346,"d":"239.76"},{"v":255.77183621534925,"d":"255.77"},{"v":268.52888768407587,"d":"268.53"},{"v":278.6120552884025,"d":"278.61"},{"v":286.55637760838647,"d":"286.56"},{"v":292.8148257945134,"d":"292.81"},{"v":297.7512367903436,"d":"297.75"},{"v":301.64885670645424,"d":"301.65"},{"v":304.7241371336592,"d":"304.72"},{"v":307.14060085279453,"d":"307.14"},{"v":309.0207215298918,"d":"309.02"},{"v":310.45533055000686,"d":"310.46"},{"v":311.5107216541676,"d":"311.51"},{"v":312.2338262668675,"d":"312.23"},{"v":312.6558353277045,"d":"312.66"},{"v":312.79457269319494,"d":"312.79"},{"v":312.6558353277045,"d":"312.66"},{"v":312.2338262668675,"d":"312.23"},{"v":311.5107216541676,"d":"311.51"},{"v":310.45533055000686,"d":"310.46"},{"v":309.0207215298918,"d":"309.02"},{"v":307.14060085279453,"d":"307.14"},{"v":304.7241371336592,"d":"304.72"},{"v":301.64885670645424,"d":"301.65"},{"v":297.7512367903436,"d":"297.75"},{"v":292.8148257945134,"d":"292.81"},{"v":286.55637760838647,"d":"286.56"},{"v":278.6120552884025,"d":"278.61"},{"v":268.52888768407587,"d":"268.53"},{"v":255.77183621534925,"d":"255.77"},{"v":239.76313240486346,"d":"239.76"},{"v":219.9732132617995,"d":"219.97"},{"v":196.07128236328586,"d":"196.07"},{"v":168.10829538810765,"d":"168.11"},{"v":138.49736270202183,"d":"138.50"},{"v":110.21483777371031,"d":"110.21"},{"v":84.23530387166129,"d":"84.24"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"},{"v":-5.37745630164491e-14,"d":"-0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":354.25724842051517,"d":"354.26"},{"v":391.01126980734296,"d":"391.01"},{"v":420.6025508629853,"d":"420.60"},{"v":443.90831032703244,"d":"443.91"},{"v":461.97310673990506,"d":"461.97"},{"v":475.7950490268102,"d":"475.80"},{"v":486.2317563124312,"d":"486.23"},{"v":493.9775269941843,"d":"493.98"},{"v":499.574564247911,"d":"499.57"},{"v":503.4363370591045,"d":"503.44"},{"v":505.8722497295274,"d":"505.87"},{"v":507.10918837800335,"d":"507.11"},{"v":507.30868218611226,"d":"507.31"},{"v":506.5797713990865,"d":"506.58"},{"v":504.9881254235944,"d":"504.99"},{"v":502.56200101355756,"d":"502.56"},{"v":499.2955174084416,"d":"499.30"},{"v":495.149562435022,"d":"495.15"},{"v":490.050476205179,"d":"490.05"},{"v":483.8865058394881,"d":"483.89"},{"v":476.50190026322525,"d":"476.50"},{"v":467.68844721091676,"d":"467.69"},{"v":457.1743108845944,"d":"457.17"},{"v":444.6103488813093,"d":"444.61"},{"v":429.5549491992247,"d":"429.55"},{"v":411.46033786551885,"d":"411.46"},{"v":389.6670766657801,"d":"389.67"},{"v":363.42011182334204,"d":"363.42"},{"v":331.9296759586386,"d":"331.93"},{"v":294.5109551850856,"d":"294.51"},{"v":250.83699383707744,"d":"250.84"},{"v":201.30639586582484,"d":"201.31"},{"v":147.43492309506172,"d":"147.43"},{"v":92.04612019377409,"d":"92.05"},{"v":41.82940077797698,"d":"41.83"},{"v":1.590318560449162,"d":"1.59"},{"v":28.959862942251586,"d":"28.96"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":211.71617382420442,"d":"211.72"},{"v":225.85221502722746,"d":"225.85"},{"v":237.11697495569118,"d":"237.12"},{"v":246.0206360140203,"d":"246.02"},{"v":253.03564915779722,"d":"253.04"},{"v":258.561997978626,"d":"258.56"},{"v":262.92095858269465,"d":"262.92"},{"v":266.36264357981315,"d":"266.36"},{"v":269.0781845345621,"d":"269.08"},{"v":271.2119756961509,"d":"271.21"},{"v":272.87216403324123,"d":"272.87"},{"v":274.1389556772525,"d":"274.14"},{"v":275.07088947466264,"d":"275.07"},{"v":275.7094069161888,"d":"275.71"},{"v":276.08205029460737,"d":"276.08"},{"v":276.204558471296,"d":"276.20"},{"v":276.08205029460737,"d":"276.08"},{"v":275.7094069161888,"d":"275.71"},{"v":275.07088947466264,"d":"275.07"},{"v":274.1389556772525,"d":"274.14"},{"v":272.87216403324123,"d":"272.87"},{"v":271.2119756961509,"d":"271.21"},{"v":269.0781845345621,"d":"269.08"},{"v":266.36264357981315,"d":"266.36"},{"v":262.92095858269465,"d":"262.92"},{"v":258.561997978626,"d":"258.56"},{"v":253.03564915779722,"d":"253.04"},{"v":246.0206360140203,"d":"246.02"},{"v":237.11697495569118,"d":"237.12"},{"v":225.85221502722746,"d":"225.85"},{"v":211.71617382420442,"d":"211.72"},{"v":194.24123545801342,"d":"194.24"},{"v":173.13529933644654,"d":"173.14"},{"v":148.44336045618562,"d":"148.44"},{"v":122.29624889326962,"d":"122.30"},{"v":97.32215089976036,"d":"97.32"},{"v":74.38164515849297,"d":"74.38"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":565.9734222447196,"d":"565.97"},{"v":616.8634848345704,"d":"616.86"},{"v":657.7195258186765,"d":"657.72"},{"v":689.9289463410528,"d":"689.93"},{"v":715.0087558977023,"d":"715.01"},{"v":734.3570470054362,"d":"734.36"},{"v":749.1527148951259,"d":"749.15"},{"v":760.3401705739975,"d":"760.34"},{"v":768.652748782473,"d":"768.65"},{"v":774.6483127552553,"d":"774.65"},{"v":778.7444137627687,"d":"778.74"},{"v":781.2481440552558,"d":"781.25"},{"v":782.3795716607749,"d":"782.38"},{"v":782.2891783152753,"d":"782.29"},{"v":781.0701757182018,"d":"781.07"},{"v":778.7665594848536,"d":"778.77"},{"v":775.377567703049,"d":"775.38"},{"v":770.8589693512108,"d":"770.86"},{"v":765.1213656798416,"d":"765.12"},{"v":758.0254615167406,"d":"758.03"},{"v":749.3740642964665,"d":"749.37"},{"v":738.9004229070677,"d":"738.90"},{"v":726.2524954191565,"d":"726.25"},{"v":710.9729924611224,"d":"710.97"},{"v":692.4759077819194,"d":"692.48"},{"v":670.0223358441449,"d":"670.02"},{"v":642.7027258235773,"d":"642.70"},{"v":609.4407478373623,"d":"609.44"},{"v":569.0466509143298,"d":"569.05"},{"v":520.3631702123131,"d":"520.36"},{"v":462.55316766128186,"d":"462.55"},{"v":395.54763132383823,"d":"395.55"},{"v":320.5702224315082,"d":"320.57"},{"v":240.48948064995972,"d":"240.49"},{"v":164.1256496712466,"d":"164.13"},{"v":98.91246946020952,"d":"98.91"},{"v":103.34150810074456,"d":"103.34"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":354.25724842051517,"d":"354.26"},{"v":391.01126980734296,"d":"391.01"},{"v":420.6025508629853,"d":"420.60"},{"v":443.90831032703244,"d":"443.91"},{"v":461.97310673990506,"d":"461.97"},{"v":475.7950490268102,"d":"475.80"},{"v":486.2317563124312,"d":"486.23"},{"v":493.9775269941843,"d":"493.98"},{"v":499.574564247911,"d":"499.57"},{"v":503.4363370591045,"d":"503.44"},{"v":505.8722497295274,"d":"505.87"},{"v":507.10918837800335,"d":"507.11"},{"v":507.30868218611226,"d":"507.31"},{"v":506.5797713990865,"d":"506.58"},{"v":504.9881254235944,"d":"504.99"},{"v":502.56200101355756,"d":"502.56"},{"v":499.2955174084416,"d":"499.30"},{"v":495.149562435022,"d":"495.15"},{"v":490.050476205179,"d":"490.05"},{"v":483.8865058394881,"d":"483.89"},{"v":476.50190026322525,"d":"476.50"},{"v":467.68844721091676,"d":"467.69"},{"v":457.1743108845944,"d":"457.17"},{"v":444.6103488813093,"d":"444.61"},{"v":429.5549491992247,"d":"429.55"},{"v":411.46033786551885,"d":"411.46"},{"v":389.6670766657801,"d":"389.67"},{"v":363.42011182334204,"d":"363.42"},{"v":331.9296759586386,"d":"331.93"},{"v":294.5109551850856,"d":"294.51"},{"v":250.83699383707744,"d":"250.84"},{"v":201.30639586582484,"d":"201.31"},{"v":147.43492309506172,"d":"147.43"},{"v":92.04612019377409,"d":"92.05"},{"v":41.82940077797698,"d":"41.83"},{"v":1.590318560449162,"d":"1.59"},{"v":28.959862942251586,"d":"28.96"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":565.9734222447196,"d":"565.97"},{"v":616.8634848345704,"d":"616.86"},{"v":657.7195258186765,"d":"657.72"},{"v":689.9289463410528,"d":"689.93"},{"v":715.0087558977023,"d":"715.01"},{"v":734.3570470054362,"d":"734.36"},{"v":749.1527148951259,"d":"749.15"},{"v":760.3401705739975,"d":"760.34"},{"v":768.652748782473,"d":"768.65"},{"v":774.6483127552553,"d":"774.65"},{"v":778.7444137627687,"d":"778.74"},{"v":781.2481440552558,"d":"781.25"},{"v":782.3795716607749,"d":"782.38"},{"v":782.2891783152753,"d":"782.29"},{"v":781.0701757182018,"d":"781.07"},{"v":778.7665594848536,"d":"778.77"},{"v":775.377567703049,"d":"775.38"},{"v":770.8589693512108,"d":"770.86"},{"v":765.1213656798416,"d":"765.12"},{"v":758.0254615167406,"d":"758.03"},{"v":749.3740642964665,"d":"749.37"},{"v":738.9004229070677,"d":"738.90"},{"v":726.2524954191565,"d":"726.25"},{"v":710.9729924611224,"d":"710.97"},{"v":692.4759077819194,"d":"692.48"},{"v":670.0223358441449,"d":"670.02"},{"v":642.7027258235773,"d":"642.70"},{"v":609.4407478373623,"d":"609.44"},{"v":569.0466509143298,"d":"569.05"},{"v":520.3631702123131,"d":"520.36"},{"v":462.55316766128186,"d":"462.55"},{"v":395.54763132383823,"d":"395.55"},{"v":320.5702224315082,"d":"320.57"},{"v":240.48948064995972,"d":"240.49"},{"v":164.1256496712466,"d":"164.13"},{"v":98.91246946020952,"d":"98.91"},{"v":103.34150810074456,"d":"103.34"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":14364.091929026283,"d":"14,364"},"W/m2"]
[null,"Total Directa disponible",{"v":14364.091929026283,"d":"14,364"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":23201.61817919323,"d":"23,202"}]
[null,"Total global ",{"v":23201.61817919323,"d":"23,202"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.380901288087409,"d":"0.381"},{"v":0.4201081683645567,"d":"0.420"}]
[]
[null,"JUNIO"]
[null,"Declinacion dia tipo",{"v":23.31440991666317,"d":"23.31"},{"v":0.4069132162053891,"d":"0.41"}]
[null,"ocaso",{"v":-111.51722978451453,"d":"-111.52"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"},{"v":-0.5130212258187674,"d":"-0.513"}]
[null,"c",{"v":-0.423301571909548,"d":"-0.423"},{"v":-0.4188962715395711,"d":"-0.419"},{"v":-0.4058142232521923,"d":"-0.406"},{"v":-0.384452918464788,"d":"-0.384"},{"v":-0.35546140961398176,"d":"-0.355"},{"v":-0.3197205890257939,"d":"-0.320"},{"v":-0.2783164234480686,"d":"-0.278"},{"v":-0.23250695750036607,"d":"-0.233"},{"v":-0.18368408862479954,"d":"-0.184"},{"v":-0.13333127498658917,"d":"-0.133"},{"v":-0.08297846134837875,"d":"-0.083"},{"v":-0.034155592472811996,"d":"-0.034"},{"v":0.011653873474890275,"d":"0.012"},{"v":0.05305803905261554,"d":"0.053"},{"v":0.0887988596408034,"d":"0.089"},{"v":0.11779036849160965,"d":"0.118"},{"v":0.1391516732790139,"d":"0.139"},{"v":0.15223372156639253,"d":"0.152"},{"v":0.1566390219363695,"d":"0.157"},{"v":0.15223372156639256,"d":"0.152"},{"v":0.13915167327901387,"d":"0.139"},{"v":0.11779036849160968,"d":"0.118"},{"v":0.08879885964080336,"d":"0.089"},{"v":0.05305803905261548,"d":"0.053"},{"v":0.01165387347489008,"d":"0.012"},{"v":-0.03415559247281222,"d":"-0.034"},{"v":-0.08297846134837875,"d":"-0.083"},{"v":-0.13333127498658928,"d":"-0.133"},{"v":-0.1836840886247997,"d":"-0.184"},{"v":-0.2325069575003663,"d":"-0.233"},{"v":-0.2783164234480686,"d":"-0.278"},{"v":-0.3197205890257939,"d":"-0.320"},{"v":-0.35546140961398187,"d":"-0.355"},{"v":-0.38445291846478824,"d":"-0.384"},{"v":-0.4058142232521923,"d":"-0.406"},{"v":-0.4188962715395711,"d":"-0.419"},{"v":-0.423301571909548,"d":"-0.423"},{"v":-0.4188962715395711,"d":"-0.419"},{"v":-0.4058142232521923,"d":"-0.406"},{"v":-0.38445291846478824,"d":"-0.384"},{"v":-0.35546140961398187,"d":"-0.355"},{"v":-0.3197205890257939,"d":"-0.320"},{"v":-0.2783164234480686,"d":"-0.278"},{"v":-0.2325069575003663,"d":"-0.233"},{"v":-0.1836840886247997,"d":"-0.184"},{"v":-0.13333127498658928,"d":"-0.133"},{"v":-0.08297846134837875,"d":"-0.083"},{"v":-0.03415559247281222,"d":"-0.034"},{"v":0.01165387347489008,"d":"0.012"},{"v":0.05305803905261548,"d":"0.053"},{"v":0.08879885964080336,"d":"0.089"},{"v":0.11779036849160968,"d":"0.118"},{"v":0.13915167327901387,"d":"0.139"},{"v":0.15223372156639256,"d":"0.152"},{"v":0.1566390219363695,"d":"0.157"},{"v":0.15223372156639253,"d":"0.152"},{"v":0.1391516732790139,"d":"0.139"},{"v":0.11779036849160965,"d":"0.118"},{"v":0.0887988596408034,"d":"0.089"},{"v":0.05305803905261554,"d":"0.053"},{"v":0.011653873474890275,"d":"0.012"},{"v":-0.034155592472811996,"d":"-0.034"},{"v":-0.08297846134837875,"d":"-0.083"},{"v":-0.13333127498658917,"d":"-0.133"},{"v":-0.18368408862479954,"d":"-0.184"},{"v":-0.23250695750036607,"d":"-0.233"},{"v":-0.2783164234480686,"d":"-0.278"},{"v":-0.3197205890257939,"d":"-0.320"},{"v":-0.35546140961398176,"d":"-0.355"},{"v":-0.384452918464788,"d":"-0.384"},{"v":-0.4058142232521923,"d":"-0.406"},{"v":-0.4188962715395711,"d":"-0.419"},{"v":-0.423301571909548,"d":"-0.423"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":18.865450530504653,"d":"18.87"},{"v":22.60945916574081,"d":"22.61"},{"v":26.991300881957656,"d":"26.99"},{"v":32.019121055782165,"d":"32.02"},{"v":37.63674725939665,"d":"37.64"},{"v":43.254373463011135,"d":"43.25"},{"v":48.28219363683567,"d":"48.28"},{"v":52.66403535305249,"d":"52.66"},{"v":56.40804398828867,"d":"56.41"},{"v":59.56463123674072,"d":"59.56"},{"v":62.20426678495892,"d":"62.20"},{"v":64.40136976075428,"d":"64.40"},{"v":66.22514597303784,"d":"66.23"},{"v":67.7356222150331,"d":"67.74"},{"v":68.98276747223797,"d":"68.98"},{"v":70.00712886691619,"d":"70.01"},{"v":70.84104075351752,"d":"70.84"},{"v":71.50992146340892,"d":"71.51"},{"v":72.03344203011231,"d":"72.03"},{"v":72.42649170158828,"d":"72.43"},{"v":72.69993008580664,"d":"72.70"},{"v":72.86114110660817,"d":"72.86"},{"v":72.91440991666319,"d":"72.91"},{"v":72.86114110660817,"d":"72.86"},{"v":72.69993008580664,"d":"72.70"},{"v":72.42649170158828,"d":"72.43"},{"v":72.03344203011231,"d":"72.03"},{"v":71.50992146340892,"d":"71.51"},{"v":70.84104075351752,"d":"70.84"},{"v":70.00712886691619,"d":"70.01"},{"v":68.98276747223797,"d":"68.98"},{"v":67.7356222150331,"d":"67.74"},{"v":66.22514597303784,"d":"66.23"},{"v":64.40136976075428,"d":"64.40"},{"v":62.20426678495892,"d":"62.20"},{"v":59.56463123674072,"d":"59.56"},{"v":56.40804398828867,"d":"56.41"},{"v":52.66403535305249,"d":"52.66"},{"v":48.28219363683567,"d":"48.28"},{"v":43.254373463011135,"d":"43.25"},{"v":37.63674725939665,"d":"37.64"},{"v":32.019121055782165,"d":"32.02"},{"v":26.991300881957656,"d":"26.99"},{"v":22.60945916574081,"d":"22.61"},{"v":18.865450530504653,"d":"18.87"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",166]
[null,"Declinacion . radianes",{"v":0.4069132162053891,"d":"0.407"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.946342832442865,"d":"1.946"}]
[null,"Distancia sol - tierra. Bo",{"v":1.0329589664737948,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":1.1498738944831546,"d":"1.150"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":12404.04027664821,"d":"12,404"}]
[null,"H1",{"v":36404.26629895897,"d":"36,404"}]
[null,"H2",{"v":0.6506163016014493,"d":"0.651"}]
[null,"H3",{"v":0.49925759288170524,"d":"0.499"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":7751.179999999999,"d":"7,751"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.6248915536490426,"d":"0.625"}]
[null,"Fraccion difusa diaria promedio",{"v":0.39129568827183714,"d":"0.391"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.8016501334486668,"d":"0.802"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.28774147006583056,"d":"0.288"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":18.865450530504653,"d":"18.87"},{"v":22.60945916574081,"d":"22.61"},{"v":26.991300881957656,"d":"26.99"},{"v":32.019121055782165,"d":"32.02"},{"v":37.63674725939665,"d":"37.64"},{"v":43.254373463011135,"d":"43.25"},{"v":48.28219363683567,"d":"48.28"},{"v":52.66403535305249,"d":"52.66"},{"v":56.40804398828867,"d":"56.41"},{"v":59.56463123674072,"d":"59.56"},{"v":62.20426678495892,"d":"62.20"},{"v":64.40136976075428,"d":"64.40"},{"v":66.22514597303784,"d":"66.23"},{"v":67.7356222150331,"d":"67.74"},{"v":68.98276747223797,"d":"68.98"},{"v":70.00712886691619,"d":"70.01"},{"v":70.84104075351752,"d":"70.84"},{"v":71.50992146340892,"d":"71.51"},{"v":72.03344203011231,"d":"72.03"},{"v":72.42649170158828,"d":"72.43"},{"v":72.69993008580664,"d":"72.70"},{"v":72.86114110660817,"d":"72.86"},{"v":72.91440991666319,"d":"72.91"},{"v":72.86114110660817,"d":"72.86"},{"v":72.69993008580664,"d":"72.70"},{"v":72.42649170158828,"d":"72.43"},{"v":72.03344203011231,"d":"72.03"},{"v":71.50992146340892,"d":"71.51"},{"v":70.84104075351752,"d":"70.84"},{"v":70.00712886691619,"d":"70.01"},{"v":68.98276747223797,"d":"68.98"},{"v":67.7356222150331,"d":"67.74"},{"v":66.22514597303784,"d":"66.23"},{"v":64.40136976075428,"d":"64.40"},{"v":62.20426678495892,"d":"62.20"},{"v":59.56463123674072,"d":"59.56"},{"v":56.40804398828867,"d":"56.41"},{"v":52.66403535305249,"d":"52.66"},{"v":48.28219363683567,"d":"48.28"},{"v":43.254373463011135,"d":"43.25"},{"v":37.63674725939665,"d":"37.64"},{"v":32.019121055782165,"d":"32.02"},{"v":26.991300881957656,"d":"26.99"},{"v":22.60945916574081,"d":"22.61"},{"v":18.865450530504653,"d":"18.87"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":111.51722978451453,"d":"111.52"},{"v":84.51597344496261,"d":"84.52"},{"v":79.45920687965294,"d":"79.46"},{"v":73.6096228785382,"d":"73.61"},{"v":66.96160352408697,"d":"66.96"},{"v":59.57675838663847,"d":"59.58"},{"v":52.190921948188276,"d":"52.19"},{"v":45.53037722376721,"d":"45.53"},{"v":39.63609947580569,"d":"39.64"},{"v":34.48112662757453,"d":"34.48"},{"v":29.995055422150703,"d":"30.00"},{"v":26.08811126815599,"d":"26.09"},{"v":22.66826254131869,"d":"22.67"},{"v":19.65067808148625,"d":"19.65"},{"v":16.961550006454754,"d":"16.96"},{"v":14.538621382416363,"d":"14.54"},{"v":12.330131672443677,"d":"12.33"},{"v":10.293189594651729,"d":"10.29"},{"v":8.392081943001445,"d":"8.39"},{"v":6.596733352975813,"d":"6.60"},{"v":4.881380252393388,"d":"4.88"},{"v":3.22345202262017,"d":"3.22"},{"v":1.602624201927968,"d":"1.60"},{"v":0,"d":"0.00"},{"v":-1.602624201927968,"d":"-1.60"},{"v":-3.22345202262017,"d":"-3.22"},{"v":-4.881380252393388,"d":"-4.88"},{"v":-6.596733352975813,"d":"-6.60"},{"v":-8.392081943001445,"d":"-8.39"},{"v":-10.293189594651729,"d":"-10.29"},{"v":-12.330131672443677,"d":"-12.33"},{"v":-14.538621382416363,"d":"-14.54"},{"v":-16.961550006454754,"d":"-16.96"},{"v":-19.65067808148625,"d":"-19.65"},{"v":-22.66826254131869,"d":"-22.67"},{"v":-26.08811126815599,"d":"-26.09"},{"v":-29.995055422150703,"d":"-30.00"},{"v":-34.48112662757453,"d":"-34.48"},{"v":-39.63609947580569,"d":"-39.64"},{"v":-45.53037722376721,"d":"-45.53"},{"v":-52.190921948188276,"d":"-52.19"},{"v":-59.57675838663847,"d":"-59.58"},{"v":-66.96160352408697,"d":"-66.96"},{"v":-73.6096228785382,"d":"-73.61"},{"v":-79.45920687965294,"d":"-79.46"},{"v":-84.51597344496261,"d":"-84.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"},{"v":-111.51722978451453,"d":"-111.52"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-0.7668646890484879,"d":"-0.77"},{"v":-0.8458288062677511,"d":"-0.85"},{"v":-0.9064377276441842,"d":"-0.91"},{"v":-0.9510389946654291,"d":"-0.95"},{"v":-0.9817882985082484,"d":"-0.98"},{"v":-0.9997122122707635,"d":"-1.00"},{"v":-1.0082306188857555,"d":"-1.01"},{"v":-1.011199879327428,"d":"-1.01"},{"v":-1.0109254458840595,"d":"-1.01"},{"v":-1.0087962815903269,"d":"-1.01"},{"v":-1.0056421231130708,"d":"-1.01"},{"v":-1.0019503773069942,"d":"-1.00"},{"v":-0.9980006119793441,"d":"-1.00"},{"v":-0.9939474039814968,"d":"-0.99"},{"v":-0.9898706423077305,"d":"-0.99"},{"v":-0.9858056475685023,"d":"-0.99"},{"v":-0.9817609829988242,"d":"-0.98"},{"v":-0.9777288352322735,"d":"-0.98"},{"v":-0.9736909140927834,"d":"-0.97"},{"v":-0.969621620717568,"d":"-0.97"},{"v":-0.965489501779757,"d":"-0.97"},{"v":-0.9612575629063395,"d":"-0.96"},{"v":-0.9568827385330229,"d":"-0.96"},{"v":-0.9523146340102395,"d":"-0.95"},{"v":-0.9474935213930299,"d":"-0.95"},{"v":-0.9423474505500933,"d":"-0.94"},{"v":-0.9367882058727947,"d":"-0.94"},{"v":-0.9307056694115361,"d":"-0.93"},{"v":-0.9239599103439831,"d":"-0.92"},{"v":-0.9163699604054737,"d":"-0.92"},{"v":-0.9076976822602328,"d":"-0.91"},{"v":-0.8976242789220663,"d":"-0.90"},{"v":-0.8857156489314315,"d":"-0.89"},{"v":-0.8713706838444524,"d":"-0.87"},{"v":-0.8537432806846307,"d":"-0.85"},{"v":-0.8316235142470031,"d":"-0.83"},{"v":-0.8032544544237654,"d":"-0.80"},{"v":-0.7660444431189781,"d":"-0.77"},{"v":-0.7160988587866115,"d":"-0.72"},{"v":-0.6474082075506297,"d":"-0.65"},{"v":-0.5503005877297077,"d":"-0.55"},{"v":-0.42069050514539674,"d":"-0.42"},{"v":-0.26053759100280693,"d":"-0.26"},{"v":-0.06443157117690176,"d":"-0.06"},{"v":0.1738099484020892,"d":"0.17"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.7668646890484879,"d":"0.77"},{"v":0.8458288062677511,"d":"0.85"},{"v":0.9064377276441842,"d":"0.91"},{"v":0.9510389946654291,"d":"0.95"},{"v":0.9817882985082484,"d":"0.98"},{"v":0.9997122122707635,"d":"1.00"},{"v":1.0082306188857555,"d":"1.01"},{"v":1.011199879327428,"d":"1.01"},{"v":1.0109254458840595,"d":"1.01"},{"v":1.0087962815903269,"d":"1.01"},{"v":1.0056421231130708,"d":"1.01"},{"v":1.0019503773069942,"d":"1.00"},{"v":0.9980006119793441,"d":"1.00"},{"v":0.9939474039814968,"d":"0.99"},{"v":0.9898706423077305,"d":"0.99"},{"v":0.9858056475685023,"d":"0.99"},{"v":0.9817609829988242,"d":"0.98"},{"v":0.9777288352322735,"d":"0.98"},{"v":0.9736909140927834,"d":"0.97"},{"v":0.969621620717568,"d":"0.97"},{"v":0.965489501779757,"d":"0.97"},{"v":0.9612575629063395,"d":"0.96"},{"v":0.9568827385330229,"d":"0.96"},{"v":0.9523146340102395,"d":"0.95"},{"v":0.9474935213930299,"d":"0.95"},{"v":0.9423474505500933,"d":"0.94"},{"v":0.9367882058727947,"d":"0.94"},{"v":0.9307056694115361,"d":"0.93"},{"v":0.9239599103439831,"d":"0.92"},{"v":0.9163699604054737,"d":"0.92"},{"v":0.9076976822602328,"d":"0.91"},{"v":0.8976242789220663,"d":"0.90"},{"v":0.8857156489314315,"d":"0.89"},{"v":0.8713706838444524,"d":"0.87"},{"v":0.8537432806846307,"d":"0.85"},{"v":0.8316235142470031,"d":"0.83"},{"v":0.8032544544237654,"d":"0.80"},{"v":0.7660444431189781,"d":"0.77"},{"v":0.7160988587866115,"d":"0.72"},{"v":0.6474082075506297,"d":"0.65"},{"v":0.5503005877297077,"d":"0.55"},{"v":0.42069050514539674,"d":"0.42"},{"v":0.26053759100280693,"d":"0.26"},{"v":0.06443157117690176,"d":"0.06"},{"v":0.1738099484020892,"d":"0.17"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":236.56882940001725,"d":"236.57"},{"v":289.7997377934636,"d":"289.80"},{"v":353.5558994657465,"d":"353.56"},{"v":427.7265158251529,"d":"427.73"},{"v":510.46368305862313,"d":"510.46"},{"v":591.3666865859471,"d":"591.37"},{"v":660.7591286553459,"d":"660.76"},{"v":717.8818629897842,"d":"717.88"},{"v":763.5701847129718,"d":"763.57"},{"v":799.4792497548066,"d":"799.48"},{"v":827.4618039725208,"d":"827.46"},{"v":849.2162614536235,"d":"849.22"},{"v":866.1510222900198,"d":"866.15"},{"v":879.371502219055,"d":"879.37"},{"v":889.7193456786946,"d":"889.72"},{"v":897.8249532558958,"d":"897.82"},{"v":904.1563337553251,"d":"904.16"},{"v":909.0588550877171,"d":"909.06"},{"v":912.7855222415768,"d":"912.79"},{"v":915.5191610263081,"d":"915.52"},{"v":917.3881963872975,"d":"917.39"},{"v":918.4774930266539,"d":"918.48"},{"v":918.8353639699233,"d":"918.84"},{"v":918.4774930266539,"d":"918.48"},{"v":917.3881963872975,"d":"917.39"},{"v":915.5191610263081,"d":"915.52"},{"v":912.7855222415768,"d":"912.79"},{"v":909.0588550877171,"d":"909.06"},{"v":904.1563337553251,"d":"904.16"},{"v":897.8249532558958,"d":"897.82"},{"v":889.7193456786946,"d":"889.72"},{"v":879.371502219055,"d":"879.37"},{"v":866.1510222900198,"d":"866.15"},{"v":849.2162614536235,"d":"849.22"},{"v":827.4618039725208,"d":"827.46"},{"v":799.4792497548066,"d":"799.48"},{"v":763.5701847129718,"d":"763.57"},{"v":717.8818629897842,"d":"717.88"},{"v":660.7591286553459,"d":"660.76"},{"v":591.3666865859471,"d":"591.37"},{"v":510.46368305862313,"d":"510.46"},{"v":427.7265158251529,"d":"427.73"},{"v":353.5558994657465,"d":"353.56"},{"v":289.7997377934636,"d":"289.80"},{"v":236.56882940001725,"d":"236.57"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"},{"v":9.538368760069473e-14,"d":"0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":111.64260460965167,"d":"111.64"},{"v":132.7390197809499,"d":"132.74"},{"v":156.70347631235984,"d":"156.70"},{"v":183.06396631371246,"d":"183.06"},{"v":210.84141669267717,"d":"210.84"},{"v":236.59366482006874,"d":"236.59"},{"v":257.72182939933424,"d":"257.72"},{"v":274.52329372099126,"d":"274.52"},{"v":287.6111658329221,"d":"287.61"},{"v":297.6938678944099,"d":"297.69"},{"v":305.43299189834374,"d":"305.43"},{"v":311.38104418763885,"d":"311.38"},{"v":315.9710314373714,"d":"315.97"},{"v":319.5303603180436,"d":"319.53"},{"v":322.3019076790197,"d":"322.30"},{"v":324.46419691519594,"d":"324.46"},{"v":326.14792439528225,"d":"326.15"},{"v":327.44852664273543,"d":"327.45"},{"v":328.43535986229597,"d":"328.44"},{"v":329.1582393704527,"d":"329.16"},{"v":329.6520006197585,"d":"329.65"},{"v":329.9395899251074,"d":"329.94"},{"v":330.03404376645767,"d":"330.03"},{"v":329.9395899251074,"d":"329.94"},{"v":329.6520006197585,"d":"329.65"},{"v":329.1582393704527,"d":"329.16"},{"v":328.43535986229597,"d":"328.44"},{"v":327.44852664273543,"d":"327.45"},{"v":326.14792439528225,"d":"326.15"},{"v":324.46419691519594,"d":"324.46"},{"v":322.3019076790197,"d":"322.30"},{"v":319.5303603180436,"d":"319.53"},{"v":315.9710314373714,"d":"315.97"},{"v":311.38104418763885,"d":"311.38"},{"v":305.43299189834374,"d":"305.43"},{"v":297.6938678944099,"d":"297.69"},{"v":287.6111658329221,"d":"287.61"},{"v":274.52329372099126,"d":"274.52"},{"v":257.72182939933424,"d":"257.72"},{"v":236.59366482006874,"d":"236.59"},{"v":210.84141669267717,"d":"210.84"},{"v":183.06396631371246,"d":"183.06"},{"v":156.70347631235984,"d":"156.70"},{"v":132.7390197809499,"d":"132.74"},{"v":111.64260460965167,"d":"111.64"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"},{"v":5.3616694079627044e-14,"d":"0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":448.3241317433845,"d":"448.32"},{"v":481.1590833838538,"d":"481.16"},{"v":506.1992273771504,"d":"506.20"},{"v":524.9741629004697,"d":"524.97"},{"v":538.8841988686426,"d":"538.88"},{"v":549.0799675697331,"d":"549.08"},{"v":556.4526496345469,"d":"556.45"},{"v":561.6698638093451,"d":"561.67"},{"v":565.2222716948099,"d":"565.22"},{"v":567.4661041549024,"d":"567.47"},{"v":568.6571889895719,"d":"568.66"},{"v":568.9764437573484,"d":"568.98"},{"v":568.5482271813975,"d":"568.55"},{"v":567.453126829531,"d":"567.45"},{"v":565.7365104134,"d":"565.74"},{"v":563.4138197281515,"d":"563.41"},{"v":560.473257793303,"d":"560.47"},{"v":556.8762377779287,"d":"556.88"},{"v":552.5557196245984,"d":"552.56"},{"v":547.4123402167627,"d":"547.41"},{"v":541.30803007205,"d":"541.31"},{"v":534.0565980903734,"d":"534.06"},{"v":525.4105735859797,"d":"525.41"},{"v":515.0434933463442,"d":"515.04"},{"v":502.52700130980145,"d":"502.53"},{"v":487.30302762714257,"d":"487.30"},{"v":468.65384106469065,"d":"468.65"},{"v":445.67859063210847,"d":"445.68"},{"v":417.2965226605175,"d":"417.30"},{"v":382.316202038565,"d":"382.32"},{"v":339.63236829753936,"d":"339.63"},{"v":288.61455004566795,"d":"288.61"},{"v":229.68296610876786,"d":"229.68"},{"v":164.8823092780871,"d":"164.88"},{"v":102.92721154412851,"d":"102.93"},{"v":51.287456111448535,"d":"51.29"},{"v":10.119668831718572,"d":"10.12"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":242.41016869133782,"d":"242.41"},{"v":253.96705059910144,"d":"253.97"},{"v":262.8703005727588,"d":"262.87"},{"v":269.70411904363687,"d":"269.70"},{"v":274.95638139008224,"d":"274.96"},{"v":279.0094421282708,"d":"279.01"},{"v":282.1524086237429,"d":"282.15"},{"v":284.5997465315893,"d":"284.60"},{"v":286.5090959765718,"d":"286.51"},{"v":287.99586475653837,"d":"288.00"},{"v":289.14432544244977,"d":"289.14"},{"v":290.0157211042948,"d":"290.02"},{"v":290.6540397735072,"d":"290.65"},{"v":291.09004192878916,"d":"291.09"},{"v":291.3439896760951,"d":"291.34"},{"v":291.42739451691904,"d":"291.43"},{"v":291.3439896760951,"d":"291.34"},{"v":291.09004192878916,"d":"291.09"},{"v":290.6540397735072,"d":"290.65"},{"v":290.0157211042948,"d":"290.02"},{"v":289.14432544244977,"d":"289.14"},{"v":287.99586475653837,"d":"288.00"},{"v":286.5090959765718,"d":"286.51"},{"v":284.5997465315893,"d":"284.60"},{"v":282.1524086237429,"d":"282.15"},{"v":279.0094421282708,"d":"279.01"},{"v":274.95638139008224,"d":"274.96"},{"v":269.70411904363687,"d":"269.70"},{"v":262.8703005727588,"d":"262.87"},{"v":253.96705059910144,"d":"253.97"},{"v":242.41016869133782,"d":"242.41"},{"v":227.57410234057573,"d":"227.57"},{"v":208.9174635163182,"d":"208.92"},{"v":186.17765616471772,"d":"186.18"},{"v":161.64955022182582,"d":"161.65"},{"v":138.37265177943473,"d":"138.37"},{"v":117.21150413460332,"d":"117.21"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":690.7343004347223,"d":"690.73"},{"v":735.1261339829553,"d":"735.13"},{"v":769.0695279499092,"d":"769.07"},{"v":794.6782819441065,"d":"794.68"},{"v":813.8405802587248,"d":"813.84"},{"v":828.0894096980039,"d":"828.09"},{"v":838.6050582582898,"d":"838.61"},{"v":846.2696103409344,"d":"846.27"},{"v":851.7313676713818,"d":"851.73"},{"v":855.4619689114407,"d":"855.46"},{"v":857.8015144320216,"d":"857.80"},{"v":858.9921648616432,"d":"858.99"},{"v":859.2022669549046,"d":"859.20"},{"v":858.5431687583202,"d":"858.54"},{"v":857.080500089495,"d":"857.08"},{"v":854.8412142450704,"d":"854.84"},{"v":851.8172474693981,"d":"851.82"},{"v":847.9662797067178,"d":"847.97"},{"v":843.2097593981056,"d":"843.21"},{"v":837.4280613210575,"d":"837.43"},{"v":830.4523555144997,"d":"830.45"},{"v":822.0524628469118,"d":"822.05"},{"v":811.9196695625515,"d":"811.92"},{"v":799.6432398779335,"d":"799.64"},{"v":784.6794099335443,"d":"784.68"},{"v":766.3124697554133,"d":"766.31"},{"v":743.6102224547728,"d":"743.61"},{"v":715.3827096757453,"d":"715.38"},{"v":680.1668232332763,"d":"680.17"},{"v":636.2832526376665,"d":"636.28"},{"v":582.0425369888771,"d":"582.04"},{"v":516.1886523862437,"d":"516.19"},{"v":438.60042962508606,"d":"438.60"},{"v":351.0599654428048,"d":"351.06"},{"v":264.5767617659543,"d":"264.58"},{"v":189.66010789088327,"d":"189.66"},{"v":127.33117296632189,"d":"127.33"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":448.3241317433845,"d":"448.32"},{"v":481.1590833838538,"d":"481.16"},{"v":506.1992273771504,"d":"506.20"},{"v":524.9741629004697,"d":"524.97"},{"v":538.8841988686426,"d":"538.88"},{"v":549.0799675697331,"d":"549.08"},{"v":556.4526496345469,"d":"556.45"},{"v":561.6698638093451,"d":"561.67"},{"v":565.2222716948099,"d":"565.22"},{"v":567.4661041549024,"d":"567.47"},{"v":568.6571889895719,"d":"568.66"},{"v":568.9764437573484,"d":"568.98"},{"v":568.5482271813975,"d":"568.55"},{"v":567.453126829531,"d":"567.45"},{"v":565.7365104134,"d":"565.74"},{"v":563.4138197281515,"d":"563.41"},{"v":560.473257793303,"d":"560.47"},{"v":556.8762377779287,"d":"556.88"},{"v":552.5557196245984,"d":"552.56"},{"v":547.4123402167627,"d":"547.41"},{"v":541.30803007205,"d":"541.31"},{"v":534.0565980903734,"d":"534.06"},{"v":525.4105735859797,"d":"525.41"},{"v":515.0434933463442,"d":"515.04"},{"v":502.52700130980145,"d":"502.53"},{"v":487.30302762714257,"d":"487.30"},{"v":468.65384106469065,"d":"468.65"},{"v":445.67859063210847,"d":"445.68"},{"v":417.2965226605175,"d":"417.30"},{"v":382.316202038565,"d":"382.32"},{"v":339.63236829753936,"d":"339.63"},{"v":288.61455004566795,"d":"288.61"},{"v":229.68296610876786,"d":"229.68"},{"v":164.8823092780871,"d":"164.88"},{"v":102.92721154412851,"d":"102.93"},{"v":51.287456111448535,"d":"51.29"},{"v":10.119668831718572,"d":"10.12"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":690.7343004347223,"d":"690.73"},{"v":735.1261339829553,"d":"735.13"},{"v":769.0695279499092,"d":"769.07"},{"v":794.6782819441065,"d":"794.68"},{"v":813.8405802587248,"d":"813.84"},{"v":828.0894096980039,"d":"828.09"},{"v":838.6050582582898,"d":"838.61"},{"v":846.2696103409344,"d":"846.27"},{"v":851.7313676713818,"d":"851.73"},{"v":855.4619689114407,"d":"855.46"},{"v":857.8015144320216,"d":"857.80"},{"v":858.9921648616432,"d":"858.99"},{"v":859.2022669549046,"d":"859.20"},{"v":858.5431687583202,"d":"858.54"},{"v":857.080500089495,"d":"857.08"},{"v":854.8412142450704,"d":"854.84"},{"v":851.8172474693981,"d":"851.82"},{"v":847.9662797067178,"d":"847.97"},{"v":843.2097593981056,"d":"843.21"},{"v":837.4280613210575,"d":"837.43"},{"v":830.4523555144997,"d":"830.45"},{"v":822.0524628469118,"d":"822.05"},{"v":811.9196695625515,"d":"811.92"},{"v":799.6432398779335,"d":"799.64"},{"v":784.6794099335443,"d":"784.68"},{"v":766.3124697554133,"d":"766.31"},{"v":743.6102224547728,"d":"743.61"},{"v":715.3827096757453,"d":"715.38"},{"v":680.1668232332763,"d":"680.17"},{"v":636.2832526376665,"d":"636.28"},{"v":582.0425369888771,"d":"582.04"},{"v":516.1886523862437,"d":"516.19"},{"v":438.60042962508606,"d":"438.60"},{"v":351.0599654428048,"d":"351.06"},{"v":264.5767617659543,"d":"264.58"},{"v":189.66010789088327,"d":"189.66"},{"v":127.33117296632189,"d":"127.33"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":16926.27494409376,"d":"16,926"},"W/m2"]
[null,"Total Directa disponible",{"v":16926.27494409376,"d":"16,926"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":26610.450659245682,"d":"26,610"}]
[null,"Total global ",{"v":26610.450659245682,"d":"26,610"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.36392377713404866,"d":"0.364"},{"v":0.39129568827183714,"d":"0.391"}]
[]
[null,"JULIO"]
[null,"Declinacion dia tipo",{"v":21.43630132294608,"d":"21.44"},{"v":0.37413403753502533,"d":"0.37"}]
[null,"ocaso",{"v":-109.52095432466217,"d":"-109.52"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"},{"v":-0.4737323625755123,"d":"-0.474"}]
[null,"c",{"v":-0.4463747528818325,"d":"-0.446"},{"v":-0.4419694525118556,"d":"-0.442"},{"v":-0.4288874042244768,"d":"-0.429"},{"v":-0.4075260994370725,"d":"-0.408"},{"v":-0.37853459058626626,"d":"-0.379"},{"v":-0.3427937699980784,"d":"-0.343"},{"v":-0.3013896044203532,"d":"-0.301"},{"v":-0.2555801384726506,"d":"-0.256"},{"v":-0.20675726959708407,"d":"-0.207"},{"v":-0.1564044559588737,"d":"-0.156"},{"v":-0.10605164232066328,"d":"-0.106"},{"v":-0.057228773445096526,"d":"-0.057"},{"v":-0.011419307497394254,"d":"-0.011"},{"v":0.02998485808033101,"d":"0.030"},{"v":0.06572567866851887,"d":"0.066"},{"v":0.09471718751932512,"d":"0.095"},{"v":0.11607849230672937,"d":"0.116"},{"v":0.129160540594108,"d":"0.129"},{"v":0.13356584096408497,"d":"0.134"},{"v":0.12916054059410803,"d":"0.129"},{"v":0.11607849230672934,"d":"0.116"},{"v":0.09471718751932515,"d":"0.095"},{"v":0.06572567866851883,"d":"0.066"},{"v":0.029984858080330953,"d":"0.030"},{"v":-0.011419307497394449,"d":"-0.011"},{"v":-0.05722877344509675,"d":"-0.057"},{"v":-0.10605164232066328,"d":"-0.106"},{"v":-0.1564044559588738,"d":"-0.156"},{"v":-0.20675726959708424,"d":"-0.207"},{"v":-0.2555801384726508,"d":"-0.256"},{"v":-0.3013896044203532,"d":"-0.301"},{"v":-0.3427937699980784,"d":"-0.343"},{"v":-0.3785345905862664,"d":"-0.379"},{"v":-0.40752609943707274,"d":"-0.408"},{"v":-0.4288874042244768,"d":"-0.429"},{"v":-0.4419694525118556,"d":"-0.442"},{"v":-0.4463747528818325,"d":"-0.446"},{"v":-0.4419694525118556,"d":"-0.442"},{"v":-0.4288874042244768,"d":"-0.429"},{"v":-0.40752609943707274,"d":"-0.408"},{"v":-0.3785345905862664,"d":"-0.379"},{"v":-0.3427937699980784,"d":"-0.343"},{"v":-0.3013896044203532,"d":"-0.301"},{"v":-0.2555801384726508,"d":"-0.256"},{"v":-0.20675726959708424,"d":"-0.207"},{"v":-0.1564044559588738,"d":"-0.156"},{"v":-0.10605164232066328,"d":"-0.106"},{"v":-0.05722877344509675,"d":"-0.057"},{"v":-0.011419307497394449,"d":"-0.011"},{"v":0.029984858080330953,"d":"0.030"},{"v":0.06572567866851883,"d":"0.066"},{"v":0.09471718751932515,"d":"0.095"},{"v":0.11607849230672934,"d":"0.116"},{"v":0.12916054059410803,"d":"0.129"},{"v":0.13356584096408497,"d":"0.134"},{"v":0.129160540594108,"d":"0.129"},{"v":0.11607849230672937,"d":"0.116"},{"v":0.09471718751932512,"d":"0.095"},{"v":0.06572567866851887,"d":"0.066"},{"v":0.02998485808033101,"d":"0.030"},{"v":-0.011419307497394254,"d":"-0.011"},{"v":-0.057228773445096526,"d":"-0.057"},{"v":-0.10605164232066328,"d":"-0.106"},{"v":-0.1564044559588737,"d":"-0.156"},{"v":-0.20675726959708407,"d":"-0.207"},{"v":-0.2555801384726506,"d":"-0.256"},{"v":-0.3013896044203532,"d":"-0.301"},{"v":-0.3427937699980784,"d":"-0.343"},{"v":-0.37853459058626626,"d":"-0.379"},{"v":-0.4075260994370725,"d":"-0.408"},{"v":-0.4288874042244768,"d":"-0.429"},{"v":-0.4419694525118556,"d":"-0.442"},{"v":-0.4463747528818325,"d":"-0.446"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":19.08596087393559,"d":"19.09"},{"v":23.579045964790808,"d":"23.58"},{"v":28.68121247752464,"d":"28.68"},{"v":34.32506185714225,"d":"34.33"},{"v":39.96891123675986,"d":"39.97"},{"v":45.07107774949371,"d":"45.07"},{"v":49.564162840348914,"d":"49.56"},{"v":53.442170163942116,"d":"53.44"},{"v":56.74225676377293,"d":"56.74"},{"v":59.524642930558706,"d":"59.52"},{"v":61.85693392715691,"d":"61.86"},{"v":63.80442176463504,"d":"63.80"},{"v":65.42529089548407,"d":"65.43"},{"v":66.768982841715,"d":"66.77"},{"v":67.87626669384517,"d":"67.88"},{"v":68.78006983973688,"d":"68.78"},{"v":69.50653928698263,"d":"69.51"},{"v":70.07607187633866,"d":"70.08"},{"v":70.50420236201836,"d":"70.50"},{"v":70.8023145921339,"d":"70.80"},{"v":70.97817519758561,"d":"70.98"},{"v":71.03630132294607,"d":"71.04"},{"v":70.97817519758561,"d":"70.98"},{"v":70.8023145921339,"d":"70.80"},{"v":70.50420236201836,"d":"70.50"},{"v":70.07607187633866,"d":"70.08"},{"v":69.50653928698263,"d":"69.51"},{"v":68.78006983973688,"d":"68.78"},{"v":67.87626669384517,"d":"67.88"},{"v":66.768982841715,"d":"66.77"},{"v":65.42529089548407,"d":"65.43"},{"v":63.80442176463504,"d":"63.80"},{"v":61.85693392715691,"d":"61.86"},{"v":59.524642930558706,"d":"59.52"},{"v":56.74225676377293,"d":"56.74"},{"v":53.442170163942116,"d":"53.44"},{"v":49.564162840348914,"d":"49.56"},{"v":45.07107774949371,"d":"45.07"},{"v":39.96891123675986,"d":"39.97"},{"v":34.32506185714225,"d":"34.33"},{"v":28.68121247752464,"d":"28.68"},{"v":23.579045964790808,"d":"23.58"},{"v":19.08596087393559,"d":"19.09"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",196.5]
[null,"Declinacion . radianes",{"v":0.37413403753502533,"d":"0.374"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.9115012528916773,"d":"1.912"}]
[null,"Distancia sol - tierra. Bo",{"v":1.032942507439385,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":1.120882831753814,"d":"1.121"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":12091.112182822633,"d":"12,091"}]
[null,"H1",{"v":36390.41160530709,"d":"36,390"}]
[null,"H2",{"v":0.6681128294546008,"d":"0.668"}]
[null,"H3",{"v":0.4527700022992131,"d":"0.453"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":8051.613333333331,"d":"8,052"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.6659117218986638,"d":"0.666"}]
[null,"Fraccion difusa diaria promedio",{"v":0.3632112287246575,"d":"0.363"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.790538745568145,"d":"0.791"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.29830127589247474,"d":"0.298"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":19.08596087393559,"d":"19.09"},{"v":23.579045964790808,"d":"23.58"},{"v":28.68121247752464,"d":"28.68"},{"v":34.32506185714225,"d":"34.33"},{"v":39.96891123675986,"d":"39.97"},{"v":45.07107774949371,"d":"45.07"},{"v":49.564162840348914,"d":"49.56"},{"v":53.442170163942116,"d":"53.44"},{"v":56.74225676377293,"d":"56.74"},{"v":59.524642930558706,"d":"59.52"},{"v":61.85693392715691,"d":"61.86"},{"v":63.80442176463504,"d":"63.80"},{"v":65.42529089548407,"d":"65.43"},{"v":66.768982841715,"d":"66.77"},{"v":67.87626669384517,"d":"67.88"},{"v":68.78006983973688,"d":"68.78"},{"v":69.50653928698263,"d":"69.51"},{"v":70.07607187633866,"d":"70.08"},{"v":70.50420236201836,"d":"70.50"},{"v":70.8023145921339,"d":"70.80"},{"v":70.97817519758561,"d":"70.98"},{"v":71.03630132294607,"d":"71.04"},{"v":70.97817519758561,"d":"70.98"},{"v":70.8023145921339,"d":"70.80"},{"v":70.50420236201836,"d":"70.50"},{"v":70.07607187633866,"d":"70.08"},{"v":69.50653928698263,"d":"69.51"},{"v":68.78006983973688,"d":"68.78"},{"v":67.87626669384517,"d":"67.88"},{"v":66.768982841715,"d":"66.77"},{"v":65.42529089548407,"d":"65.43"},{"v":63.80442176463504,"d":"63.80"},{"v":61.85693392715691,"d":"61.86"},{"v":59.524642930558706,"d":"59.52"},{"v":56.74225676377293,"d":"56.74"},{"v":53.442170163942116,"d":"53.44"},{"v":49.564162840348914,"d":"49.56"},{"v":45.07107774949371,"d":"45.07"},{"v":39.96891123675986,"d":"39.97"},{"v":34.32506185714225,"d":"34.33"},{"v":28.68121247752464,"d":"28.68"},{"v":23.579045964790808,"d":"23.58"},{"v":19.08596087393559,"d":"19.09"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":109.52095432466216,"d":"109.52"},{"v":82.69597907884578,"d":"82.70"},{"v":76.69377166075849,"d":"76.69"},{"v":69.94616285973036,"d":"69.95"},{"v":62.526719855072564,"d":"62.53"},{"v":55.10638355599661,"d":"55.11"},{"v":48.34728256746317,"d":"48.35"},{"v":42.30326396459307,"d":"42.30"},{"v":36.963674523302714,"d":"36.96"},{"v":32.27354154927673,"d":"32.27"},{"v":28.155192630194836,"d":"28.16"},{"v":24.524811838528986,"d":"24.52"},{"v":21.302439987447524,"d":"21.30"},{"v":18.41669235747961,"d":"18.42"},{"v":15.806119854664475,"d":"15.81"},{"v":13.418785726058509,"d":"13.42"},{"v":11.211065573574961,"d":"11.21"},{"v":9.146224288483417,"d":"9.15"},{"v":7.19303392702558,"d":"7.19"},{"v":5.324534646741535,"d":"5.32"},{"v":3.516958822545171,"d":"3.52"},{"v":1.74880084300563,"d":"1.75"},{"v":0,"d":"0.00"},{"v":-1.74880084300563,"d":"-1.75"},{"v":-3.516958822545171,"d":"-3.52"},{"v":-5.324534646741535,"d":"-5.32"},{"v":-7.19303392702558,"d":"-7.19"},{"v":-9.146224288483417,"d":"-9.15"},{"v":-11.211065573574961,"d":"-11.21"},{"v":-13.418785726058509,"d":"-13.42"},{"v":-15.806119854664475,"d":"-15.81"},{"v":-18.41669235747961,"d":"-18.42"},{"v":-21.302439987447524,"d":"-21.30"},{"v":-24.524811838528986,"d":"-24.52"},{"v":-28.155192630194836,"d":"-28.16"},{"v":-32.27354154927673,"d":"-32.27"},{"v":-36.963674523302714,"d":"-36.96"},{"v":-42.30326396459307,"d":"-42.30"},{"v":-48.34728256746317,"d":"-48.35"},{"v":-55.10638355599661,"d":"-55.11"},{"v":-62.526719855072564,"d":"-62.53"},{"v":-69.94616285973036,"d":"-69.95"},{"v":-76.69377166075849,"d":"-76.69"},{"v":-82.69597907884578,"d":"-82.70"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"},{"v":-109.52095432466216,"d":"-109.52"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-0.8529553823426268,"d":"-0.85"},{"v":-0.9263058202585762,"d":"-0.93"},{"v":-0.9767125423804164,"d":"-0.98"},{"v":-1.0096983961885349,"d":"-1.01"},{"v":-1.0283359723025323,"d":"-1.03"},{"v":-1.0370250649552544,"d":"-1.04"},{"v":-1.0399188245529865,"d":"-1.04"},{"v":-1.0394353924356012,"d":"-1.04"},{"v":-1.0370142885582028,"d":"-1.04"},{"v":-1.0335136244433973,"d":"-1.03"},{"v":-1.0294394516507972,"d":"-1.03"},{"v":-1.025084157007924,"d":"-1.03"},{"v":-1.0206108849549502,"d":"-1.02"},{"v":-1.016104833714511,"d":"-1.02"},{"v":-1.0116041613980853,"d":"-1.01"},{"v":-1.0071184215962043,"d":"-1.01"},{"v":-1.0026394093478557,"d":"-1.00"},{"v":-0.9981473807545218,"d":"-1.00"},{"v":-0.9936144179699888,"d":"-0.99"},{"v":-0.9890059794279691,"d":"-0.99"},{"v":-0.9842812250989221,"d":"-0.98"},{"v":-0.9793924233691081,"d":"-0.98"},{"v":-0.9742835567768034,"d":"-0.97"},{"v":-0.9688881010440504,"d":"-0.97"},{"v":-0.9631258224785388,"d":"-0.96"},{"v":-0.9568982954972668,"d":"-0.96"},{"v":-0.9500826562577277,"d":"-0.95"},{"v":-0.9425228437470736,"d":"-0.94"},{"v":-0.93401718320064,"d":"-0.93"},{"v":-0.9243005562870056,"d":"-0.92"},{"v":-0.913018446839622,"d":"-0.91"},{"v":-0.8996886357554946,"d":"-0.90"},{"v":-0.8836438844810593,"d":"-0.88"},{"v":-0.863944958213142,"d":"-0.86"},{"v":-0.8392465695354426,"d":"-0.84"},{"v":-0.807586580727983,"d":"-0.81"},{"v":-0.7660444431189782,"d":"-0.77"},{"v":-0.7101606361365586,"d":"-0.71"},{"v":-0.6328755437163842,"d":"-0.63"},{"v":-0.5223904900494213,"d":"-0.52"},{"v":-0.3705133082318557,"d":"-0.37"},{"v":-0.17283236274653796,"d":"-0.17"},{"v":0.08653737191387423,"d":"0.09"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.8529553823426268,"d":"0.85"},{"v":0.9263058202585762,"d":"0.93"},{"v":0.9767125423804164,"d":"0.98"},{"v":1.0096983961885349,"d":"1.01"},{"v":1.0283359723025323,"d":"1.03"},{"v":1.0370250649552544,"d":"1.04"},{"v":1.0399188245529865,"d":"1.04"},{"v":1.0394353924356012,"d":"1.04"},{"v":1.0370142885582028,"d":"1.04"},{"v":1.0335136244433973,"d":"1.03"},{"v":1.0294394516507972,"d":"1.03"},{"v":1.025084157007924,"d":"1.03"},{"v":1.0206108849549502,"d":"1.02"},{"v":1.016104833714511,"d":"1.02"},{"v":1.0116041613980853,"d":"1.01"},{"v":1.0071184215962043,"d":"1.01"},{"v":1.0026394093478557,"d":"1.00"},{"v":0.9981473807545218,"d":"1.00"},{"v":0.9936144179699888,"d":"0.99"},{"v":0.9890059794279691,"d":"0.99"},{"v":0.9842812250989221,"d":"0.98"},{"v":0.9793924233691081,"d":"0.98"},{"v":0.9742835567768034,"d":"0.97"},{"v":0.9688881010440504,"d":"0.97"},{"v":0.9631258224785388,"d":"0.96"},{"v":0.9568982954972668,"d":"0.96"},{"v":0.9500826562577277,"d":"0.95"},{"v":0.9425228437470736,"d":"0.94"},{"v":0.93401718320064,"d":"0.93"},{"v":0.9243005562870056,"d":"0.92"},{"v":0.913018446839622,"d":"0.91"},{"v":0.8996886357554946,"d":"0.90"},{"v":0.8836438844810593,"d":"0.88"},{"v":0.863944958213142,"d":"0.86"},{"v":0.8392465695354426,"d":"0.84"},{"v":0.807586580727983,"d":"0.81"},{"v":0.7660444431189782,"d":"0.77"},{"v":0.7101606361365586,"d":"0.71"},{"v":0.6328755437163842,"d":"0.63"},{"v":0.5223904900494213,"d":"0.52"},{"v":0.3705133082318557,"d":"0.37"},{"v":0.17283236274653796,"d":"0.17"},{"v":0.08653737191387423,"d":"0.09"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":254.72061074066,"d":"254.72"},{"v":323.1676167392542,"d":"323.17"},{"v":402.9135742723238,"d":"402.91"},{"v":492.123867309389,"d":"492.12"},{"v":580.5692924580532,"d":"580.57"},{"v":658.2490115148726,"d":"658.25"},{"v":723.6719142297045,"d":"723.67"},{"v":777.1105757429004,"d":"777.11"},{"v":819.8983837477671,"d":"819.90"},{"v":853.7758954064235,"d":"853.78"},{"v":880.4666057418805,"d":"880.47"},{"v":901.4738189860115,"d":"901.47"},{"v":918.0216808761386,"d":"918.02"},{"v":931.0688143733327,"d":"931.07"},{"v":941.3492075527224,"d":"941.35"},{"v":949.4173448684616,"d":"949.42"},{"v":955.688112442513,"d":"955.69"},{"v":960.4687932368713,"d":"960.47"},{"v":963.983348258052,"d":"963.98"},{"v":966.3901288068715,"d":"966.39"},{"v":967.7942707879331,"d":"967.79"},{"v":968.2558116428032,"d":"968.26"},{"v":967.7942707879331,"d":"967.79"},{"v":966.3901288068715,"d":"966.39"},{"v":963.983348258052,"d":"963.98"},{"v":960.4687932368713,"d":"960.47"},{"v":955.688112442513,"d":"955.69"},{"v":949.4173448684616,"d":"949.42"},{"v":941.3492075527224,"d":"941.35"},{"v":931.0688143733327,"d":"931.07"},{"v":918.0216808761386,"d":"918.02"},{"v":901.4738189860115,"d":"901.47"},{"v":880.4666057418805,"d":"880.47"},{"v":853.7758954064235,"d":"853.78"},{"v":819.8983837477671,"d":"819.90"},{"v":777.1105757429004,"d":"777.11"},{"v":723.6719142297045,"d":"723.67"},{"v":658.2490115148726,"d":"658.25"},{"v":580.5692924580532,"d":"580.57"},{"v":492.123867309389,"d":"492.12"},{"v":402.9135742723238,"d":"402.91"},{"v":323.1676167392542,"d":"323.17"},{"v":254.72061074066,"d":"254.72"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"},{"v":-1.0224726562082261e-13,"d":"-0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":111.67352191982188,"d":"111.67"},{"v":136.61413846793982,"d":"136.61"},{"v":163.9093710788024,"d":"163.91"},{"v":192.58077711341684,"d":"192.58"},{"v":219.38508430975435,"d":"219.39"},{"v":241.79297833881134,"d":"241.79"},{"v":259.9447279741105,"d":"259.94"},{"v":274.33082790388954,"d":"274.33"},{"v":285.58606437345463,"d":"285.59"},{"v":294.34112990323774,"d":"294.34"},{"v":301.146057367804,"d":"301.15"},{"v":306.44645311568644,"d":"306.45"},{"v":310.5882215510445,"d":"310.59"},{"v":313.83343685096924,"d":"313.83"},{"v":316.37804873146274,"d":"316.38"},{"v":318.36750667268274,"d":"318.37"},{"v":319.9092114429263,"d":"319.91"},{"v":321.0819147210309,"d":"321.08"},{"v":321.9425803966194,"d":"321.94"},{"v":322.5312586917797,"d":"322.53"},{"v":322.874434667795,"d":"322.87"},{"v":322.9871938347854,"d":"322.99"},{"v":322.874434667795,"d":"322.87"},{"v":322.5312586917797,"d":"322.53"},{"v":321.9425803966194,"d":"321.94"},{"v":321.0819147210309,"d":"321.08"},{"v":319.9092114429263,"d":"319.91"},{"v":318.36750667268274,"d":"318.37"},{"v":316.37804873146274,"d":"316.38"},{"v":313.83343685096924,"d":"313.83"},{"v":310.5882215510445,"d":"310.59"},{"v":306.44645311568644,"d":"306.45"},{"v":301.146057367804,"d":"301.15"},{"v":294.34112990323774,"d":"294.34"},{"v":285.58606437345463,"d":"285.59"},{"v":274.33082790388954,"d":"274.33"},{"v":259.9447279741105,"d":"259.94"},{"v":241.79297833881134,"d":"241.79"},{"v":219.38508430975435,"d":"219.39"},{"v":192.58077711341684,"d":"192.58"},{"v":163.9093710788024,"d":"163.91"},{"v":136.61413846793982,"d":"136.61"},{"v":111.67352191982188,"d":"111.67"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"},{"v":-5.375518407376308e-14,"d":"-0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":482.2386304441811,"d":"482.24"},{"v":522.6070645037149,"d":"522.61"},{"v":554.0895097438358,"d":"554.09"},{"v":578.1834521348396,"d":"578.18"},{"v":596.3754276482484,"d":"596.38"},{"v":609.9531257398277,"d":"609.95"},{"v":619.9532004730311,"d":"619.95"},{"v":627.1758506400746,"d":"627.18"},{"v":632.22342501737,"d":"632.22"},{"v":635.541916992273,"d":"635.54"},{"v":637.4569817740545,"d":"637.46"},{"v":638.2023380793958,"d":"638.20"},{"v":637.9409638716421,"d":"637.94"},{"v":636.7802724515619,"d":"636.78"},{"v":634.7824863869257,"d":"634.78"},{"v":631.9711953190293,"d":"631.97"},{"v":628.3347917710414,"d":"628.33"},{"v":623.8271980061792,"d":"623.83"},{"v":618.3660426112949,"d":"618.37"},{"v":611.8282142151256,"d":"611.83"},{"v":604.0425070543063,"d":"604.04"},{"v":594.7788880424162,"d":"594.78"},{"v":583.7338013438728,"d":"583.73"},{"v":570.5110028039404,"d":"570.51"},{"v":554.5979535914161,"d":"554.60"},{"v":535.3393590370582,"d":"535.34"},{"v":511.9130597249664,"d":"511.91"},{"v":483.32084510562873,"d":"483.32"},{"v":448.41978109541753,"d":"448.42"},{"v":406.0381774165843,"d":"406.04"},{"v":355.2356341542972,"d":"355.24"},{"v":295.7506814432194,"d":"295.75"},{"v":228.5846521136263,"d":"228.58"},{"v":156.4784616783919,"d":"156.48"},{"v":88.55423800655026,"d":"88.55"},{"v":32.24247842821619,"d":"32.24"},{"v":12.378919126485867,"d":"12.38"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":229.5369711783761,"d":"229.54"},{"v":242.24021709794638,"d":"242.24"},{"v":252.17884100947913,"d":"252.18"},{"v":259.9097584234871,"d":"259.91"},{"v":265.9186605907996,"d":"265.92"},{"v":270.5990278192392,"d":"270.60"},{"v":274.25630138421405,"d":"274.26"},{"v":277.12189860779245,"d":"277.12"},{"v":279.3688474435125,"d":"279.37"},{"v":281.12558301446774,"d":"281.13"},{"v":282.48694258567707,"d":"282.49"},{"v":283.52246563953906,"d":"283.52"},{"v":284.28245255641724,"d":"284.28"},{"v":284.8022685723936,"d":"284.80"},{"v":285.1053005851204,"d":"285.11"},{"v":285.2048694352575,"d":"285.20"},{"v":285.1053005851204,"d":"285.11"},{"v":284.8022685723936,"d":"284.80"},{"v":284.28245255641724,"d":"284.28"},{"v":283.52246563953906,"d":"283.52"},{"v":282.48694258567707,"d":"282.49"},{"v":281.12558301446774,"d":"281.13"},{"v":279.3688474435125,"d":"279.37"},{"v":277.12189860779245,"d":"277.12"},{"v":274.25630138421405,"d":"274.26"},{"v":270.5990278192392,"d":"270.60"},{"v":265.9186605907996,"d":"265.92"},{"v":259.9097584234871,"d":"259.91"},{"v":252.17884100947913,"d":"252.18"},{"v":242.24021709794638,"d":"242.24"},{"v":229.5369711783761,"d":"229.54"},{"v":213.50857289022258,"d":"213.51"},{"v":193.72190452421506,"d":"193.72"},{"v":170.05310563634214,"d":"170.05"},{"v":144.73561698442273,"d":"144.74"},{"v":120.63332004639587,"d":"120.63"},{"v":98.6102014150134,"d":"98.61"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":711.7756016225572,"d":"711.78"},{"v":764.8472816016613,"d":"764.85"},{"v":806.268350753315,"d":"806.27"},{"v":838.0932105583267,"d":"838.09"},{"v":862.294088239048,"d":"862.29"},{"v":880.5521535590669,"d":"880.55"},{"v":894.2095018572452,"d":"894.21"},{"v":904.297749247867,"d":"904.30"},{"v":911.5922724608824,"d":"911.59"},{"v":916.6675000067407,"d":"916.67"},{"v":919.9439243597316,"d":"919.94"},{"v":921.7248037189348,"d":"921.72"},{"v":922.2234164280594,"d":"922.22"},{"v":921.5825410239555,"d":"921.58"},{"v":919.8877869720461,"d":"919.89"},{"v":917.1760647542868,"d":"917.18"},{"v":913.4400923561618,"d":"913.44"},{"v":908.6294665785728,"d":"908.63"},{"v":902.6484951677121,"d":"902.65"},{"v":895.3506798546647,"d":"895.35"},{"v":886.5294496399833,"d":"886.53"},{"v":875.904471056884,"d":"875.90"},{"v":863.1026487873853,"d":"863.10"},{"v":847.6329014117329,"d":"847.63"},{"v":828.85425497563,"d":"828.85"},{"v":805.9383868562975,"d":"805.94"},{"v":777.831720315766,"d":"777.83"},{"v":743.2306035291158,"d":"743.23"},{"v":700.5986221048967,"d":"700.60"},{"v":648.2783945145306,"d":"648.28"},{"v":584.7726053326733,"d":"584.77"},{"v":509.25925433344196,"d":"509.26"},{"v":422.30655663784137,"d":"422.31"},{"v":326.53156731473405,"d":"326.53"},{"v":233.289854990973,"d":"233.29"},{"v":152.87579847461205,"d":"152.88"},{"v":110.98912054149928,"d":"110.99"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":482.2386304441811,"d":"482.24"},{"v":522.6070645037149,"d":"522.61"},{"v":554.0895097438358,"d":"554.09"},{"v":578.1834521348396,"d":"578.18"},{"v":596.3754276482484,"d":"596.38"},{"v":609.9531257398277,"d":"609.95"},{"v":619.9532004730311,"d":"619.95"},{"v":627.1758506400746,"d":"627.18"},{"v":632.22342501737,"d":"632.22"},{"v":635.541916992273,"d":"635.54"},{"v":637.4569817740545,"d":"637.46"},{"v":638.2023380793958,"d":"638.20"},{"v":637.9409638716421,"d":"637.94"},{"v":636.7802724515619,"d":"636.78"},{"v":634.7824863869257,"d":"634.78"},{"v":631.9711953190293,"d":"631.97"},{"v":628.3347917710414,"d":"628.33"},{"v":623.8271980061792,"d":"623.83"},{"v":618.3660426112949,"d":"618.37"},{"v":611.8282142151256,"d":"611.83"},{"v":604.0425070543063,"d":"604.04"},{"v":594.7788880424162,"d":"594.78"},{"v":583.7338013438728,"d":"583.73"},{"v":570.5110028039404,"d":"570.51"},{"v":554.5979535914161,"d":"554.60"},{"v":535.3393590370582,"d":"535.34"},{"v":511.9130597249664,"d":"511.91"},{"v":483.32084510562873,"d":"483.32"},{"v":448.41978109541753,"d":"448.42"},{"v":406.0381774165843,"d":"406.04"},{"v":355.2356341542972,"d":"355.24"},{"v":295.7506814432194,"d":"295.75"},{"v":228.5846521136263,"d":"228.58"},{"v":156.4784616783919,"d":"156.48"},{"v":88.55423800655026,"d":"88.55"},{"v":32.24247842821619,"d":"32.24"},{"v":12.378919126485867,"d":"12.38"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":711.7756016225572,"d":"711.78"},{"v":764.8472816016613,"d":"764.85"},{"v":806.268350753315,"d":"806.27"},{"v":838.0932105583267,"d":"838.09"},{"v":862.294088239048,"d":"862.29"},{"v":880.5521535590669,"d":"880.55"},{"v":894.2095018572452,"d":"894.21"},{"v":904.297749247867,"d":"904.30"},{"v":911.5922724608824,"d":"911.59"},{"v":916.6675000067407,"d":"916.67"},{"v":919.9439243597316,"d":"919.94"},{"v":921.7248037189348,"d":"921.72"},{"v":922.2234164280594,"d":"922.22"},{"v":921.5825410239555,"d":"921.58"},{"v":919.8877869720461,"d":"919.89"},{"v":917.1760647542868,"d":"917.18"},{"v":913.4400923561618,"d":"913.44"},{"v":908.6294665785728,"d":"908.63"},{"v":902.6484951677121,"d":"902.65"},{"v":895.3506798546647,"d":"895.35"},{"v":886.5294496399833,"d":"886.53"},{"v":875.904471056884,"d":"875.90"},{"v":863.1026487873853,"d":"863.10"},{"v":847.6329014117329,"d":"847.63"},{"v":828.85425497563,"d":"828.85"},{"v":805.9383868562975,"d":"805.94"},{"v":777.831720315766,"d":"777.83"},{"v":743.2306035291158,"d":"743.23"},{"v":700.5986221048967,"d":"700.60"},{"v":648.2783945145306,"d":"648.28"},{"v":584.7726053326733,"d":"584.77"},{"v":509.25925433344196,"d":"509.26"},{"v":422.30655663784137,"d":"422.31"},{"v":326.53156731473405,"d":"326.53"},{"v":233.289854990973,"d":"233.29"},{"v":152.87579847461205,"d":"152.88"},{"v":110.98912054149928,"d":"110.99"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":18619.752527990036,"d":"18,620"},"W/m2"]
[null,"Total Directa disponible",{"v":18619.752527990036,"d":"18,620"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":27951.131191938843,"d":"27,951"}]
[null,"Total global ",{"v":27951.131191938843,"d":"27,951"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.33384619033379204,"d":"0.334"},{"v":0.3632112287246575,"d":"0.363"}]
[]
[null,"AGOSTO"]
[null,"Declinacion dia tipo",{"v":13.619766412491641,"d":"13.62"},{"v":0.2377097672505153,"d":"0.24"}]
[null,"ocaso",{"v":-101.90007842438935,"d":"-101.90"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"},{"v":-0.3052351977424064,"d":"-0.305"}]
[null,"c",{"v":-0.5244909809007721,"d":"-0.524"},{"v":-0.5200856805307952,"d":"-0.520"},{"v":-0.5070036322434164,"d":"-0.507"},{"v":-0.48564232745601216,"d":"-0.486"},{"v":-0.4566508186052059,"d":"-0.457"},{"v":-0.42090999801701806,"d":"-0.421"},{"v":-0.3795058324392928,"d":"-0.380"},{"v":-0.33369636649159024,"d":"-0.334"},{"v":-0.2848734976160237,"d":"-0.285"},{"v":-0.23452068397781334,"d":"-0.235"},{"v":-0.1841678703396029,"d":"-0.184"},{"v":-0.13534500146403616,"d":"-0.135"},{"v":-0.08953553551633389,"d":"-0.090"},{"v":-0.04813136993860863,"d":"-0.048"},{"v":-0.012390549350420763,"d":"-0.012"},{"v":0.01660095950038548,"d":"0.017"},{"v":0.037962264287789725,"d":"0.038"},{"v":0.05104431257516837,"d":"0.051"},{"v":0.05544961294514533,"d":"0.055"},{"v":0.05104431257516838,"d":"0.051"},{"v":0.037962264287789704,"d":"0.038"},{"v":0.016600959500385516,"d":"0.017"},{"v":-0.012390549350420804,"d":"-0.012"},{"v":-0.048131369938608684,"d":"-0.048"},{"v":-0.08953553551633409,"d":"-0.090"},{"v":-0.13534500146403639,"d":"-0.135"},{"v":-0.1841678703396029,"d":"-0.184"},{"v":-0.23452068397781345,"d":"-0.235"},{"v":-0.2848734976160239,"d":"-0.285"},{"v":-0.33369636649159046,"d":"-0.334"},{"v":-0.3795058324392928,"d":"-0.380"},{"v":-0.42090999801701806,"d":"-0.421"},{"v":-0.456650818605206,"d":"-0.457"},{"v":-0.4856423274560124,"d":"-0.486"},{"v":-0.5070036322434164,"d":"-0.507"},{"v":-0.5200856805307952,"d":"-0.520"},{"v":-0.5244909809007721,"d":"-0.524"},{"v":-0.5200856805307952,"d":"-0.520"},{"v":-0.5070036322434164,"d":"-0.507"},{"v":-0.4856423274560124,"d":"-0.486"},{"v":-0.456650818605206,"d":"-0.457"},{"v":-0.42090999801701806,"d":"-0.421"},{"v":-0.3795058324392928,"d":"-0.380"},{"v":-0.33369636649159046,"d":"-0.334"},{"v":-0.2848734976160239,"d":"-0.285"},{"v":-0.23452068397781345,"d":"-0.235"},{"v":-0.1841678703396029,"d":"-0.184"},{"v":-0.13534500146403639,"d":"-0.135"},{"v":-0.08953553551633409,"d":"-0.090"},{"v":-0.048131369938608684,"d":"-0.048"},{"v":-0.012390549350420804,"d":"-0.012"},{"v":0.016600959500385516,"d":"0.017"},{"v":0.037962264287789704,"d":"0.038"},{"v":0.05104431257516838,"d":"0.051"},{"v":0.05544961294514533,"d":"0.055"},{"v":0.05104431257516837,"d":"0.051"},{"v":0.037962264287789725,"d":"0.038"},{"v":0.01660095950038548,"d":"0.017"},{"v":-0.012390549350420763,"d":"-0.012"},{"v":-0.04813136993860863,"d":"-0.048"},{"v":-0.08953553551633389,"d":"-0.090"},{"v":-0.13534500146403616,"d":"-0.135"},{"v":-0.1841678703396029,"d":"-0.184"},{"v":-0.23452068397781334,"d":"-0.235"},{"v":-0.2848734976160237,"d":"-0.285"},{"v":-0.33369636649159024,"d":"-0.334"},{"v":-0.3795058324392928,"d":"-0.380"},{"v":-0.42090999801701806,"d":"-0.421"},{"v":-0.4566508186052059,"d":"-0.457"},{"v":-0.48564232745601216,"d":"-0.486"},{"v":-0.5070036322434164,"d":"-0.507"},{"v":-0.5200856805307952,"d":"-0.520"},{"v":-0.5244909809007721,"d":"-0.524"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":10.222732610973168,"d":"10.22"},{"v":15.573527004199107,"d":"15.57"},{"v":21.304465653205753,"d":"21.30"},{"v":27.035404302212395,"d":"27.04"},{"v":32.386198695438345,"d":"32.39"},{"v":37.256027420163996,"d":"37.26"},{"v":41.59531177861728,"d":"41.60"},{"v":45.39833365475762,"d":"45.40"},{"v":48.690083798218815,"d":"48.69"},{"v":51.51292734242331,"d":"51.51"},{"v":53.916146184616906,"d":"53.92"},{"v":55.949064051106376,"d":"55.95"},{"v":57.65718751923832,"d":"57.66"},{"v":59.08043497466377,"d":"59.08"},{"v":60.25262619933771,"d":"60.25"},{"v":61.20164120636112,"d":"61.20"},{"v":61.94987570499673,"d":"61.95"},{"v":62.514778673358165,"d":"62.51"},{"v":62.909357938633434,"d":"62.91"},{"v":63.14259808314401,"d":"63.14"},{"v":63.21976641249164,"d":"63.22"},{"v":63.14259808314401,"d":"63.14"},{"v":62.909357938633434,"d":"62.91"},{"v":62.514778673358165,"d":"62.51"},{"v":61.94987570499673,"d":"61.95"},{"v":61.20164120636112,"d":"61.20"},{"v":60.25262619933771,"d":"60.25"},{"v":59.08043497466377,"d":"59.08"},{"v":57.65718751923832,"d":"57.66"},{"v":55.949064051106376,"d":"55.95"},{"v":53.916146184616906,"d":"53.92"},{"v":51.51292734242331,"d":"51.51"},{"v":48.690083798218815,"d":"48.69"},{"v":45.39833365475762,"d":"45.40"},{"v":41.59531177861728,"d":"41.60"},{"v":37.256027420163996,"d":"37.26"},{"v":32.386198695438345,"d":"32.39"},{"v":27.035404302212395,"d":"27.04"},{"v":21.304465653205753,"d":"21.30"},{"v":15.573527004199107,"d":"15.57"},{"v":10.222732610973168,"d":"10.22"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",227.5]
[null,"Declinacion . radianes",{"v":0.2377097672505153,"d":"0.238"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.7784918765460298,"d":"1.778"}]
[null,"Distancia sol - tierra. Bo",{"v":1.0329229440105085,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":0.9956466553880514,"d":"0.996"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":10739.969478381681,"d":"10,740"}]
[null,"H1",{"v":36708.54518317241,"d":"36,709"}]
[null,"H2",{"v":0.724217495577656,"d":"0.724"}]
[null,"H3",{"v":0.2714291598103954,"d":"0.271"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":7010.111111111111,"d":"7,010"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.6527123866805818,"d":"0.653"}]
[null,"Fraccion difusa diaria promedio",{"v":0.35487154647976893,"d":"0.355"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.7439853208473751,"d":"0.744"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.3425437351516274,"d":"0.343"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":10.222732610973168,"d":"10.22"},{"v":15.573527004199107,"d":"15.57"},{"v":21.304465653205753,"d":"21.30"},{"v":27.035404302212395,"d":"27.04"},{"v":32.386198695438345,"d":"32.39"},{"v":37.256027420163996,"d":"37.26"},{"v":41.59531177861728,"d":"41.60"},{"v":45.39833365475762,"d":"45.40"},{"v":48.690083798218815,"d":"48.69"},{"v":51.51292734242331,"d":"51.51"},{"v":53.916146184616906,"d":"53.92"},{"v":55.949064051106376,"d":"55.95"},{"v":57.65718751923832,"d":"57.66"},{"v":59.08043497466377,"d":"59.08"},{"v":60.25262619933771,"d":"60.25"},{"v":61.20164120636112,"d":"61.20"},{"v":61.94987570499673,"d":"61.95"},{"v":62.514778673358165,"d":"62.51"},{"v":62.909357938633434,"d":"62.91"},{"v":63.14259808314401,"d":"63.14"},{"v":63.21976641249164,"d":"63.22"},{"v":63.14259808314401,"d":"63.14"},{"v":62.909357938633434,"d":"62.91"},{"v":62.514778673358165,"d":"62.51"},{"v":61.94987570499673,"d":"61.95"},{"v":61.20164120636112,"d":"61.20"},{"v":60.25262619933771,"d":"60.25"},{"v":59.08043497466377,"d":"59.08"},{"v":57.65718751923832,"d":"57.66"},{"v":55.949064051106376,"d":"55.95"},{"v":53.916146184616906,"d":"53.92"},{"v":51.51292734242331,"d":"51.51"},{"v":48.690083798218815,"d":"48.69"},{"v":45.39833365475762,"d":"45.40"},{"v":41.59531177861728,"d":"41.60"},{"v":37.256027420163996,"d":"37.26"},{"v":32.386198695438345,"d":"32.39"},{"v":27.035404302212395,"d":"27.04"},{"v":21.304465653205753,"d":"21.30"},{"v":15.573527004199107,"d":"15.57"},{"v":10.222732610973168,"d":"10.22"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":101.90007842438935,"d":"101.90"},{"v":88.07531586378276,"d":"88.08"},{"v":80.99401845853576,"d":"80.99"},{"v":73.45964625449825,"d":"73.46"},{"v":65.9247330207515,"d":"65.92"},{"v":58.83603847155746,"d":"58.84"},{"v":52.284886042894115,"d":"52.28"},{"v":46.30974684279447,"d":"46.31"},{"v":40.904380568753794,"d":"40.90"},{"v":36.03164520043154,"d":"36.03"},{"v":31.63725653999378,"d":"31.64"},{"v":27.660425889658953,"d":"27.66"},{"v":24.040723335708492,"d":"24.04"},{"v":20.72180007583076,"d":"20.72"},{"v":17.65295087602508,"d":"17.65"},{"v":14.789376722490397,"d":"14.79"},{"v":12.091754476510104,"d":"12.09"},{"v":9.525489459669721,"d":"9.53"},{"v":7.059861039467049,"d":"7.06"},{"v":4.667165892583653,"d":"4.67"},{"v":2.3219017263130506,"d":"2.32"},{"v":0,"d":"0.00"},{"v":-2.3219017263130506,"d":"-2.32"},{"v":-4.667165892583653,"d":"-4.67"},{"v":-7.059861039467049,"d":"-7.06"},{"v":-9.525489459669721,"d":"-9.53"},{"v":-12.091754476510104,"d":"-12.09"},{"v":-14.789376722490397,"d":"-14.79"},{"v":-17.65295087602508,"d":"-17.65"},{"v":-20.72180007583076,"d":"-20.72"},{"v":-24.040723335708492,"d":"-24.04"},{"v":-27.660425889658953,"d":"-27.66"},{"v":-31.63725653999378,"d":"-31.64"},{"v":-36.03164520043154,"d":"-36.03"},{"v":-40.904380568753794,"d":"-40.90"},{"v":-46.30974684279447,"d":"-46.31"},{"v":-52.284886042894115,"d":"-52.28"},{"v":-58.83603847155746,"d":"-58.84"},{"v":-65.9247330207515,"d":"-65.92"},{"v":-73.45964625449825,"d":"-73.46"},{"v":-80.99401845853576,"d":"-80.99"},{"v":-88.07531586378276,"d":"-88.08"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"},{"v":-101.90007842438935,"d":"-101.90"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-1.1232271610234639,"d":"-1.12"},{"v":-1.174181552121677,"d":"-1.17"},{"v":-1.192652086723459,"d":"-1.19"},{"v":-1.1968588080146683,"d":"-1.20"},{"v":-1.1943303062728474,"d":"-1.19"},{"v":-1.1886064836012336,"d":"-1.19"},{"v":-1.181375981663119,"d":"-1.18"},{"v":-1.1735149366937307,"d":"-1.17"},{"v":-1.1654889588052666,"d":"-1.17"},{"v":-1.1575388120368963,"d":"-1.16"},{"v":-1.149777350627891,"d":"-1.15"},{"v":-1.1422438321349242,"d":"-1.14"},{"v":-1.1349353031487885,"d":"-1.13"},{"v":-1.1278248100757635,"d":"-1.13"},{"v":-1.1208717895995708,"d":"-1.12"},{"v":-1.1140277419464126,"d":"-1.11"},{"v":-1.1072390179787484,"d":"-1.11"},{"v":-1.100447793403928,"d":"-1.10"},{"v":-1.093591838481045,"d":"-1.09"},{"v":-1.0866033974433158,"d":"-1.09"},{"v":-1.0794072947111069,"d":"-1.08"},{"v":-1.0719182372519664,"d":"-1.07"},{"v":-1.0640371503767652,"d":"-1.06"},{"v":-1.0556462395763706,"d":"-1.06"},{"v":-1.0466022839025813,"d":"-1.05"},{"v":-1.0367273977866414,"d":"-1.04"},{"v":-1.0257960886576176,"d":"-1.03"},{"v":-1.0135167890369237,"d":"-1.01"},{"v":-0.9995049826010414,"d":"-1.00"},{"v":-0.9832432616363075,"d":"-0.98"},{"v":-0.9640205520413259,"d":"-0.96"},{"v":-0.9408371217569489,"d":"-0.94"},{"v":-0.9122512832625314,"d":"-0.91"},{"v":-0.876122029550374,"d":"-0.88"},{"v":-0.8291546520366048,"d":"-0.83"},{"v":-0.766044443118978,"d":"-0.77"},{"v":-0.6777198819470335,"d":"-0.68"},{"v":-0.5473142576701087,"d":"-0.55"},{"v":-0.33943679951449734,"d":"-0.34"},{"v":0.015458426496434821,"d":"0.02"},{"v":0.6978296592394582,"d":"0.70"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":1.1232271610234639,"d":"1.12"},{"v":1.174181552121677,"d":"1.17"},{"v":1.192652086723459,"d":"1.19"},{"v":1.1968588080146683,"d":"1.20"},{"v":1.1943303062728474,"d":"1.19"},{"v":1.1886064836012336,"d":"1.19"},{"v":1.181375981663119,"d":"1.18"},{"v":1.1735149366937307,"d":"1.17"},{"v":1.1654889588052666,"d":"1.17"},{"v":1.1575388120368963,"d":"1.16"},{"v":1.149777350627891,"d":"1.15"},{"v":1.1422438321349242,"d":"1.14"},{"v":1.1349353031487885,"d":"1.13"},{"v":1.1278248100757635,"d":"1.13"},{"v":1.1208717895995708,"d":"1.12"},{"v":1.1140277419464126,"d":"1.11"},{"v":1.1072390179787484,"d":"1.11"},{"v":1.100447793403928,"d":"1.10"},{"v":1.093591838481045,"d":"1.09"},{"v":1.0866033974433158,"d":"1.09"},{"v":1.0794072947111069,"d":"1.08"},{"v":1.0719182372519664,"d":"1.07"},{"v":1.0640371503767652,"d":"1.06"},{"v":1.0556462395763706,"d":"1.06"},{"v":1.0466022839025813,"d":"1.05"},{"v":1.0367273977866414,"d":"1.04"},{"v":1.0257960886576176,"d":"1.03"},{"v":1.0135167890369237,"d":"1.01"},{"v":0.9995049826010414,"d":"1.00"},{"v":0.9832432616363075,"d":"0.98"},{"v":0.9640205520413259,"d":"0.96"},{"v":0.9408371217569489,"d":"0.94"},{"v":0.9122512832625314,"d":"0.91"},{"v":0.876122029550374,"d":"0.88"},{"v":0.8291546520366048,"d":"0.83"},{"v":0.766044443118978,"d":"0.77"},{"v":0.6777198819470335,"d":"0.68"},{"v":0.5473142576701087,"d":"0.55"},{"v":0.33943679951449734,"d":"0.34"},{"v":0.015458426496434821,"d":"0.02"},{"v":0.6978296592394582,"d":"0.70"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":123.57330816860453,"d":"123.57"},{"v":197.3560040570008,"d":"197.36"},{"v":281.7789409064933,"d":"281.78"},{"v":370.2087677881078,"d":"370.21"},{"v":454.77265696305597,"d":"454.77"},{"v":532.0100085608608,"d":"532.01"},{"v":599.9709855706689,"d":"599.97"},{"v":658.0988627691974,"d":"658.10"},{"v":706.8214187816421,"d":"706.82"},{"v":747.1055631317711,"d":"747.11"},{"v":780.1142982928988,"d":"780.11"},{"v":806.9953038261226,"d":"807.00"},{"v":828.7751977906743,"d":"828.78"},{"v":846.3213922397339,"d":"846.32"},{"v":860.3405101363838,"d":"860.34"},{"v":871.3932481335522,"d":"871.39"},{"v":879.914376857211,"d":"879.91"},{"v":886.232241195717,"d":"886.23"},{"v":890.5853237064457,"d":"890.59"},{"v":893.1350565548998,"d":"893.14"},{"v":893.974788379984,"d":"893.97"},{"v":893.1350565548998,"d":"893.14"},{"v":890.5853237064457,"d":"890.59"},{"v":886.232241195717,"d":"886.23"},{"v":879.914376857211,"d":"879.91"},{"v":871.3932481335522,"d":"871.39"},{"v":860.3405101363838,"d":"860.34"},{"v":846.3213922397339,"d":"846.32"},{"v":828.7751977906743,"d":"828.78"},{"v":806.9953038261226,"d":"807.00"},{"v":780.1142982928988,"d":"780.11"},{"v":747.1055631317711,"d":"747.11"},{"v":706.8214187816421,"d":"706.82"},{"v":658.0988627691974,"d":"658.10"},{"v":599.9709855706689,"d":"599.97"},{"v":532.0100085608608,"d":"532.01"},{"v":454.77265696305597,"d":"454.77"},{"v":370.2087677881078,"d":"370.21"},{"v":281.7789409064933,"d":"281.78"},{"v":197.3560040570008,"d":"197.36"},{"v":123.57330816860453,"d":"123.57"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":58.045316407667265,"d":"58.05"},{"v":87.80777121455034,"d":"87.81"},{"v":118.82925518838807,"d":"118.83"},{"v":148.66287299063998,"d":"148.66"},{"v":175.1818118861758,"d":"175.18"},{"v":197.99576811103861,"d":"198.00"},{"v":217.12471403202073,"d":"217.12"},{"v":232.86965357901386,"d":"232.87"},{"v":245.67223889369743,"d":"245.67"},{"v":256.0069569827583,"d":"256.01"},{"v":264.3167069514138,"d":"264.32"},{"v":270.9836054378671,"d":"270.98"},{"v":276.32196816034616,"d":"276.32"},{"v":280.58265618233173,"d":"280.58"},{"v":283.9618767161329,"d":"283.96"},{"v":286.61072232225223,"d":"286.61"},{"v":288.6437584523673,"d":"288.64"},{"v":290.1460698757869,"d":"290.15"},{"v":291.17869797843247,"d":"291.18"},{"v":291.78260479648384,"d":"291.78"},{"v":291.98134547321337,"d":"291.98"},{"v":291.78260479648384,"d":"291.78"},{"v":291.17869797843247,"d":"291.18"},{"v":290.1460698757869,"d":"290.15"},{"v":288.6437584523673,"d":"288.64"},{"v":286.61072232225223,"d":"286.61"},{"v":283.9618767161329,"d":"283.96"},{"v":280.58265618233173,"d":"280.58"},{"v":276.32196816034616,"d":"276.32"},{"v":270.9836054378671,"d":"270.98"},{"v":264.3167069514138,"d":"264.32"},{"v":256.0069569827583,"d":"256.01"},{"v":245.67223889369743,"d":"245.67"},{"v":232.86965357901386,"d":"232.87"},{"v":217.12471403202073,"d":"217.12"},{"v":197.99576811103861,"d":"198.00"},{"v":175.1818118861758,"d":"175.18"},{"v":148.66287299063998,"d":"148.66"},{"v":118.82925518838807,"d":"118.83"},{"v":87.80777121455034,"d":"87.81"},{"v":58.045316407667265,"d":"58.05"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":397.01149181380003,"d":"397.01"},{"v":452.2853898650355,"d":"452.29"},{"v":499.0128285031434,"d":"499.01"},{"v":537.4642775215033,"d":"537.46"},{"v":568.4656971547039,"d":"568.47"},{"v":593.0523880328602,"d":"593.05"},{"v":612.2560564361502,"d":"612.26"},{"v":626.9986736460237,"d":"627.00"},{"v":638.054182546442,"d":"638.05"},{"v":646.0465503287116,"d":"646.05"},{"v":651.4639567592824,"d":"651.46"},{"v":654.6778988822663,"d":"654.68"},{"v":655.961711907613,"d":"655.96"},{"v":655.5061938276177,"d":"655.51"},{"v":653.4316171415625,"d":"653.43"},{"v":649.7961136418226,"d":"649.80"},{"v":644.6006600560295,"d":"644.60"},{"v":637.7909179565875,"d":"637.79"},{"v":629.2561252173605,"d":"629.26"},{"v":618.8251796270009,"d":"618.83"},{"v":606.2600662554486,"d":"606.26"},{"v":591.2469477483162,"d":"591.25"},{"v":573.3857072027058,"d":"573.39"},{"v":552.1797556695502,"d":"552.18"},{"v":527.0298905984852,"d":"527.03"},{"v":497.2394787466046,"d":"497.24"},{"v":462.0437991080866,"d":"462.04"},{"v":420.68393112824145,"d":"420.68"},{"v":372.5526777798041,"d":"372.55"},{"v":317.4387670611393,"d":"317.44"},{"v":255.86975281919246,"d":"255.87"},{"v":189.48427451897456,"d":"189.48"},{"v":121.2552269509361,"d":"121.26"},{"v":55.31111980204684,"d":"55.31"},{"v":1.6934433052093474,"d":"1.69"},{"v":45.727376161180864,"d":"45.73"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":174.83466301678675,"d":"174.83"},{"v":191.72594734002368,"d":"191.73"},{"v":205.6290788371294,"d":"205.63"},{"v":216.93404616340618,"d":"216.93"},{"v":226.05983188959976,"d":"226.06"},{"v":233.39752576752582,"d":"233.40"},{"v":239.2845452799454,"d":"239.28"},{"v":243.99843819063923,"d":"244.00"},{"v":247.76072039318484,"d":"247.76"},{"v":250.7446472160814,"d":"250.74"},{"v":253.08363674776498,"d":"253.08"},{"v":254.8788528278899,"d":"254.88"},{"v":256.2054271984721,"d":"256.21"},{"v":257.1172607597149,"d":"257.12"},{"v":257.65052389980553,"d":"257.65"},{"v":257.8260163336855,"d":"257.83"},{"v":257.65052389980553,"d":"257.65"},{"v":257.1172607597149,"d":"257.12"},{"v":256.2054271984721,"d":"256.21"},{"v":254.8788528278899,"d":"254.88"},{"v":253.08363674776498,"d":"253.08"},{"v":250.7446472160814,"d":"250.74"},{"v":247.76072039318484,"d":"247.76"},{"v":243.99843819063923,"d":"244.00"},{"v":239.2845452799454,"d":"239.28"},{"v":233.39752576752582,"d":"233.40"},{"v":226.05983188959976,"d":"226.06"},{"v":216.93404616340618,"d":"216.93"},{"v":205.6290788371294,"d":"205.63"},{"v":191.72594734002368,"d":"191.73"},{"v":174.83466301678675,"d":"174.83"},{"v":154.68943270854746,"d":"154.69"},{"v":131.27262037161105,"d":"131.27"},{"v":104.92887290270987,"d":"104.93"},{"v":77.53621320805959,"d":"77.54"},{"v":51.255304245421804,"d":"51.26"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":571.8461548305868,"d":"571.85"},{"v":644.0113372050591,"d":"644.01"},{"v":704.6419073402728,"d":"704.64"},{"v":754.3983236849094,"d":"754.40"},{"v":794.5255290443037,"d":"794.53"},{"v":826.4499138003861,"d":"826.45"},{"v":851.5406017160956,"d":"851.54"},{"v":870.997111836663,"d":"871.00"},{"v":885.8149029396268,"d":"885.81"},{"v":896.791197544793,"d":"896.79"},{"v":904.5475935070474,"d":"904.55"},{"v":909.5567517101562,"d":"909.56"},{"v":912.1671391060851,"d":"912.17"},{"v":912.6234545873326,"d":"912.62"},{"v":911.082141041368,"d":"911.08"},{"v":907.6221299755081,"d":"907.62"},{"v":902.251183955835,"d":"902.25"},{"v":894.9081787163024,"d":"894.91"},{"v":885.4615524158326,"d":"885.46"},{"v":873.7040324548908,"d":"873.70"},{"v":859.3437030032136,"d":"859.34"},{"v":841.9915949643976,"d":"841.99"},{"v":821.1464275958906,"d":"821.15"},{"v":796.1781938601895,"d":"796.18"},{"v":766.3144358784306,"d":"766.31"},{"v":730.6370045141305,"d":"730.64"},{"v":688.1036309976864,"d":"688.10"},{"v":637.6179772916477,"d":"637.62"},{"v":578.1817566169335,"d":"578.18"},{"v":509.164714401163,"d":"509.16"},{"v":430.7044158359792,"d":"430.70"},{"v":344.173707227522,"d":"344.17"},{"v":252.52784732254716,"d":"252.53"},{"v":160.2399927047567,"d":"160.24"},{"v":79.22965651326894,"d":"79.23"},{"v":96.98268040660267,"d":"96.98"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":397.01149181380003,"d":"397.01"},{"v":452.2853898650355,"d":"452.29"},{"v":499.0128285031434,"d":"499.01"},{"v":537.4642775215033,"d":"537.46"},{"v":568.4656971547039,"d":"568.47"},{"v":593.0523880328602,"d":"593.05"},{"v":612.2560564361502,"d":"612.26"},{"v":626.9986736460237,"d":"627.00"},{"v":638.054182546442,"d":"638.05"},{"v":646.0465503287116,"d":"646.05"},{"v":651.4639567592824,"d":"651.46"},{"v":654.6778988822663,"d":"654.68"},{"v":655.961711907613,"d":"655.96"},{"v":655.5061938276177,"d":"655.51"},{"v":653.4316171415625,"d":"653.43"},{"v":649.7961136418226,"d":"649.80"},{"v":644.6006600560295,"d":"644.60"},{"v":637.7909179565875,"d":"637.79"},{"v":629.2561252173605,"d":"629.26"},{"v":618.8251796270009,"d":"618.83"},{"v":606.2600662554486,"d":"606.26"},{"v":591.2469477483162,"d":"591.25"},{"v":573.3857072027058,"d":"573.39"},{"v":552.1797556695502,"d":"552.18"},{"v":527.0298905984852,"d":"527.03"},{"v":497.2394787466046,"d":"497.24"},{"v":462.0437991080866,"d":"462.04"},{"v":420.68393112824145,"d":"420.68"},{"v":372.5526777798041,"d":"372.55"},{"v":317.4387670611393,"d":"317.44"},{"v":255.86975281919246,"d":"255.87"},{"v":189.48427451897456,"d":"189.48"},{"v":121.2552269509361,"d":"121.26"},{"v":55.31111980204684,"d":"55.31"},{"v":1.6934433052093474,"d":"1.69"},{"v":45.727376161180864,"d":"45.73"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":571.8461548305868,"d":"571.85"},{"v":644.0113372050591,"d":"644.01"},{"v":704.6419073402728,"d":"704.64"},{"v":754.3983236849094,"d":"754.40"},{"v":794.5255290443037,"d":"794.53"},{"v":826.4499138003861,"d":"826.45"},{"v":851.5406017160956,"d":"851.54"},{"v":870.997111836663,"d":"871.00"},{"v":885.8149029396268,"d":"885.81"},{"v":896.791197544793,"d":"896.79"},{"v":904.5475935070474,"d":"904.55"},{"v":909.5567517101562,"d":"909.56"},{"v":912.1671391060851,"d":"912.17"},{"v":912.6234545873326,"d":"912.62"},{"v":911.082141041368,"d":"911.08"},{"v":907.6221299755081,"d":"907.62"},{"v":902.251183955835,"d":"902.25"},{"v":894.9081787163024,"d":"894.91"},{"v":885.4615524158326,"d":"885.46"},{"v":873.7040324548908,"d":"873.70"},{"v":859.3437030032136,"d":"859.34"},{"v":841.9915949643976,"d":"841.99"},{"v":821.1464275958906,"d":"821.15"},{"v":796.1781938601895,"d":"796.18"},{"v":766.3144358784306,"d":"766.31"},{"v":730.6370045141305,"d":"730.64"},{"v":688.1036309976864,"d":"688.10"},{"v":637.6179772916477,"d":"637.62"},{"v":578.1817566169335,"d":"578.18"},{"v":509.164714401163,"d":"509.16"},{"v":430.7044158359792,"d":"430.70"},{"v":344.173707227522,"d":"344.17"},{"v":252.52784732254716,"d":"252.53"},{"v":160.2399927047567,"d":"160.24"},{"v":79.22965651326894,"d":"79.23"},{"v":96.98268040660267,"d":"96.98"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":17611.360125721432,"d":"17,611"},"W/m2"]
[null,"Total Directa disponible",{"v":17611.360125721432,"d":"17,611"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":25407.478876547415,"d":"25,407"}]
[null,"Total global ",{"v":25407.478876547415,"d":"25,407"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.3068434608843562,"d":"0.307"},{"v":0.35487154647976893,"d":"0.355"}]
[]
[null,"SEPTIEMBRE"]
[null,"Declinacion dia tipo",{"v":2.216886783213346,"d":"2.22"},{"v":0.03869197351101864,"d":"0.04"}]
[null,"ocaso",{"v":-91.88800227320753,"d":"-91.89"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"},{"v":-0.05014156300727873,"d":"-0.050"}]
[null,"c",{"v":-0.5784442719543118,"d":"-0.578"},{"v":-0.5740389715843349,"d":"-0.574"},{"v":-0.5609569232969561,"d":"-0.561"},{"v":-0.5395956185095518,"d":"-0.540"},{"v":-0.5106041096587456,"d":"-0.511"},{"v":-0.47486328907055775,"d":"-0.475"},{"v":-0.4334591234928325,"d":"-0.433"},{"v":-0.3876496575451299,"d":"-0.388"},{"v":-0.3388267886695634,"d":"-0.339"},{"v":-0.288473975031353,"d":"-0.288"},{"v":-0.2381211613931426,"d":"-0.238"},{"v":-0.18929829251757585,"d":"-0.189"},{"v":-0.14348882656987358,"d":"-0.143"},{"v":-0.1020846609921483,"d":"-0.102"},{"v":-0.06634384040396044,"d":"-0.066"},{"v":-0.03735233155315419,"d":"-0.037"},{"v":-0.01599102676574995,"d":"-0.016"},{"v":-0.002908978478371304,"d":"-0.003"},{"v":0.0014963218916056568,"d":"0.001"},{"v":-0.0029089784783712935,"d":"-0.003"},{"v":-0.015991026765749972,"d":"-0.016"},{"v":-0.03735233155315416,"d":"-0.037"},{"v":-0.06634384040396048,"d":"-0.066"},{"v":-0.10208466099214836,"d":"-0.102"},{"v":-0.14348882656987377,"d":"-0.143"},{"v":-0.18929829251757607,"d":"-0.189"},{"v":-0.2381211613931426,"d":"-0.238"},{"v":-0.28847397503135314,"d":"-0.288"},{"v":-0.33882678866956356,"d":"-0.339"},{"v":-0.38764965754513014,"d":"-0.388"},{"v":-0.4334591234928325,"d":"-0.433"},{"v":-0.47486328907055775,"d":"-0.475"},{"v":-0.5106041096587457,"d":"-0.511"},{"v":-0.5395956185095521,"d":"-0.540"},{"v":-0.5609569232969561,"d":"-0.561"},{"v":-0.5740389715843349,"d":"-0.574"},{"v":-0.5784442719543118,"d":"-0.578"},{"v":-0.5740389715843349,"d":"-0.574"},{"v":-0.5609569232969561,"d":"-0.561"},{"v":-0.5395956185095521,"d":"-0.540"},{"v":-0.5106041096587457,"d":"-0.511"},{"v":-0.47486328907055775,"d":"-0.475"},{"v":-0.4334591234928325,"d":"-0.433"},{"v":-0.38764965754513014,"d":"-0.388"},{"v":-0.33882678866956356,"d":"-0.339"},{"v":-0.28847397503135314,"d":"-0.288"},{"v":-0.2381211613931426,"d":"-0.238"},{"v":-0.18929829251757607,"d":"-0.189"},{"v":-0.14348882656987377,"d":"-0.143"},{"v":-0.10208466099214836,"d":"-0.102"},{"v":-0.06634384040396048,"d":"-0.066"},{"v":-0.03735233155315416,"d":"-0.037"},{"v":-0.015991026765749972,"d":"-0.016"},{"v":-0.0029089784783712935,"d":"-0.003"},{"v":0.0014963218916056568,"d":"0.001"},{"v":-0.002908978478371304,"d":"-0.003"},{"v":-0.01599102676574995,"d":"-0.016"},{"v":-0.03735233155315419,"d":"-0.037"},{"v":-0.06634384040396044,"d":"-0.066"},{"v":-0.1020846609921483,"d":"-0.102"},{"v":-0.14348882656987358,"d":"-0.143"},{"v":-0.18929829251757585,"d":"-0.189"},{"v":-0.2381211613931426,"d":"-0.238"},{"v":-0.288473975031353,"d":"-0.288"},{"v":-0.3388267886695634,"d":"-0.339"},{"v":-0.3876496575451299,"d":"-0.388"},{"v":-0.4334591234928325,"d":"-0.433"},{"v":-0.47486328907055775,"d":"-0.475"},{"v":-0.5106041096587456,"d":"-0.511"},{"v":-0.5395956185095518,"d":"-0.540"},{"v":-0.5609569232969561,"d":"-0.561"},{"v":-0.5740389715843349,"d":"-0.574"},{"v":-0.5784442719543118,"d":"-0.578"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":3.421668770329432,"d":"3.42"},{"v":9.25098832512882,"d":"9.25"},{"v":14.884621350607713,"d":"14.88"},{"v":20.188583508382532,"d":"20.19"},{"v":25.068451596431913,"d":"25.07"},{"v":29.47209568185623,"d":"29.47"},{"v":33.38390419898243,"d":"33.38"},{"v":36.81490056435912,"d":"36.81"},{"v":39.792580696422725,"d":"39.79"},{"v":42.352591728594135,"d":"42.35"},{"v":44.5328556557421,"d":"44.53"},{"v":46.36988291365827,"d":"46.37"},{"v":47.896718648499494,"d":"47.90"},{"v":49.14196937919065,"d":"49.14"},{"v":50.12947734468758,"d":"50.13"},{"v":50.87834259932652,"d":"50.88"},{"v":51.40310060820364,"d":"51.40"},{"v":51.71393903221907,"d":"51.71"},{"v":51.81688678321335,"d":"51.82"},{"v":51.71393903221907,"d":"51.71"},{"v":51.40310060820364,"d":"51.40"},{"v":50.87834259932652,"d":"50.88"},{"v":50.12947734468758,"d":"50.13"},{"v":49.14196937919065,"d":"49.14"},{"v":47.896718648499494,"d":"47.90"},{"v":46.36988291365827,"d":"46.37"},{"v":44.5328556557421,"d":"44.53"},{"v":42.352591728594135,"d":"42.35"},{"v":39.792580696422725,"d":"39.79"},{"v":36.81490056435912,"d":"36.81"},{"v":33.38390419898243,"d":"33.38"},{"v":29.47209568185623,"d":"29.47"},{"v":25.068451596431913,"d":"25.07"},{"v":20.188583508382532,"d":"20.19"},{"v":14.884621350607713,"d":"14.88"},{"v":9.25098832512882,"d":"9.25"},{"v":3.421668770329432,"d":"3.42"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",258]
[null,"Declinacion . radianes",{"v":0.03869197351101864,"d":"0.039"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.6037481827475057,"d":"1.604"}]
[null,"Distancia sol - tierra. Bo",{"v":1.032900908903918,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":0.8007624595289455,"d":"0.801"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":8637.583286113353,"d":"8,638"}]
[null,"H1",{"v":37262.937128863916,"d":"37,263"}]
[null,"H2",{"v":0.7605552392524241,"d":"0.761"}]
[null,"H3",{"v":0.04020722027652141,"d":"0.040"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":5477.901111111111,"d":"5,478"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.6341937240614438,"d":"0.634"}]
[null,"Fraccion difusa diaria promedio",{"v":0.34371547018839144,"d":"0.344"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.6739754911810394,"d":"0.674"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.4090781964792634,"d":"0.409"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":3.421668770329432,"d":"3.42"},{"v":9.25098832512882,"d":"9.25"},{"v":14.884621350607713,"d":"14.88"},{"v":20.188583508382532,"d":"20.19"},{"v":25.068451596431913,"d":"25.07"},{"v":29.47209568185623,"d":"29.47"},{"v":33.38390419898243,"d":"33.38"},{"v":36.81490056435912,"d":"36.81"},{"v":39.792580696422725,"d":"39.79"},{"v":42.352591728594135,"d":"42.35"},{"v":44.5328556557421,"d":"44.53"},{"v":46.36988291365827,"d":"46.37"},{"v":47.896718648499494,"d":"47.90"},{"v":49.14196937919065,"d":"49.14"},{"v":50.12947734468758,"d":"50.13"},{"v":50.87834259932652,"d":"50.88"},{"v":51.40310060820364,"d":"51.40"},{"v":51.71393903221907,"d":"51.71"},{"v":51.81688678321335,"d":"51.82"},{"v":51.71393903221907,"d":"51.71"},{"v":51.40310060820364,"d":"51.40"},{"v":50.87834259932652,"d":"50.88"},{"v":50.12947734468758,"d":"50.13"},{"v":49.14196937919065,"d":"49.14"},{"v":47.896718648499494,"d":"47.90"},{"v":46.36988291365827,"d":"46.37"},{"v":44.5328556557421,"d":"44.53"},{"v":42.352591728594135,"d":"42.35"},{"v":39.792580696422725,"d":"39.79"},{"v":36.81490056435912,"d":"36.81"},{"v":33.38390419898243,"d":"33.38"},{"v":29.47209568185623,"d":"29.47"},{"v":25.068451596431913,"d":"25.07"},{"v":20.188583508382532,"d":"20.19"},{"v":14.884621350607713,"d":"14.88"},{"v":9.25098832512882,"d":"9.25"},{"v":3.421668770329432,"d":"3.42"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":91.88800227320755,"d":"91.89"},{"v":87.39296669727705,"d":"87.39"},{"v":79.72862080461594,"d":"79.73"},{"v":72.26497750047172,"d":"72.26"},{"v":65.12942447799854,"d":"65.13"},{"v":58.40943506720886,"d":"58.41"},{"v":52.149863345656726,"d":"52.15"},{"v":46.35873334236743,"d":"46.36"},{"v":41.01710397930169,"d":"41.02"},{"v":36.089174156121004,"d":"36.09"},{"v":31.530509985850227,"d":"31.53"},{"v":27.293795290308946,"d":"27.29"},{"v":23.33236398777547,"d":"23.33"},{"v":19.602072572330524,"d":"19.60"},{"v":16.06206315232957,"d":"16.06"},{"v":12.674845524872191,"d":"12.67"},{"v":9.405992026849203,"d":"9.41"},{"v":6.2236296147899415,"d":"6.22"},{"v":3.0978364362590183,"d":"3.10"},{"v":0,"d":"0.00"},{"v":-3.0978364362590183,"d":"-3.10"},{"v":-6.2236296147899415,"d":"-6.22"},{"v":-9.405992026849203,"d":"-9.41"},{"v":-12.674845524872191,"d":"-12.67"},{"v":-16.06206315232957,"d":"-16.06"},{"v":-19.602072572330524,"d":"-19.60"},{"v":-23.33236398777547,"d":"-23.33"},{"v":-27.293795290308946,"d":"-27.29"},{"v":-31.530509985850227,"d":"-31.53"},{"v":-36.089174156121004,"d":"-36.09"},{"v":-41.01710397930169,"d":"-41.02"},{"v":-46.35873334236743,"d":"-46.36"},{"v":-52.149863345656726,"d":"-52.15"},{"v":-58.40943506720886,"d":"-58.41"},{"v":-65.12942447799854,"d":"-65.13"},{"v":-72.26497750047172,"d":"-72.26"},{"v":-79.72862080461594,"d":"-79.73"},{"v":-87.39296669727705,"d":"-87.39"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"},{"v":-91.88800227320755,"d":"-91.89"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-3.548522023073471,"d":"-3.55"},{"v":-2.1158046587984853,"d":"-2.12"},{"v":-1.7880983241767812,"d":"-1.79"},{"v":-1.6401046207833507,"d":"-1.64"},{"v":-1.5542381684595306,"d":"-1.55"},{"v":-1.4971609712737277,"d":"-1.50"},{"v":-1.4557809573135703,"d":"-1.46"},{"v":-1.4238975410793966,"d":"-1.42"},{"v":-1.3981847511484875,"d":"-1.40"},{"v":-1.376690262892976,"d":"-1.38"},{"v":-1.358185681499023,"d":"-1.36"},{"v":-1.3418532850035683,"d":"-1.34"},{"v":-1.3271218222324688,"d":"-1.33"},{"v":-1.3135743852979536,"d":"-1.31"},{"v":-1.300893616619841,"d":"-1.30"},{"v":-1.288827324615917,"d":"-1.29"},{"v":-1.277165700532349,"d":"-1.28"},{"v":-1.265725261803842,"d":"-1.27"},{"v":-1.254336637273979,"d":"-1.25"},{"v":-1.242834330922193,"d":"-1.24"},{"v":-1.231047094308594,"d":"-1.23"},{"v":-1.2187876991589566,"d":"-1.22"},{"v":-1.205840794875068,"d":"-1.21"},{"v":-1.1919471316026458,"d":"-1.19"},{"v":-1.176781591607638,"d":"-1.18"},{"v":-1.1599208883780876,"d":"-1.16"},{"v":-1.140793801101474,"d":"-1.14"},{"v":-1.1186009715450154,"d":"-1.12"},{"v":-1.0921793041844183,"d":"-1.09"},{"v":-1.059759791977284,"d":"-1.06"},{"v":-1.0185055292319245,"d":"-1.02"},{"v":-0.9635545551109574,"d":"-0.96"},{"v":-0.885811583481515,"d":"-0.89"},{"v":-0.7660444431189773,"d":"-0.77"},{"v":-0.5552682576204588,"d":"-0.56"},{"v":-0.08075322178617093,"d":"-0.08"},{"v":2.0164331368355133,"d":"2.02"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":3.548522023073471,"d":"3.55"},{"v":2.1158046587984853,"d":"2.12"},{"v":1.7880983241767812,"d":"1.79"},{"v":1.6401046207833507,"d":"1.64"},{"v":1.5542381684595306,"d":"1.55"},{"v":1.4971609712737277,"d":"1.50"},{"v":1.4557809573135703,"d":"1.46"},{"v":1.4238975410793966,"d":"1.42"},{"v":1.3981847511484875,"d":"1.40"},{"v":1.376690262892976,"d":"1.38"},{"v":1.358185681499023,"d":"1.36"},{"v":1.3418532850035683,"d":"1.34"},{"v":1.3271218222324688,"d":"1.33"},{"v":1.3135743852979536,"d":"1.31"},{"v":1.300893616619841,"d":"1.30"},{"v":1.288827324615917,"d":"1.29"},{"v":1.277165700532349,"d":"1.28"},{"v":1.265725261803842,"d":"1.27"},{"v":1.254336637273979,"d":"1.25"},{"v":1.242834330922193,"d":"1.24"},{"v":1.231047094308594,"d":"1.23"},{"v":1.2187876991589566,"d":"1.22"},{"v":1.205840794875068,"d":"1.21"},{"v":1.1919471316026458,"d":"1.19"},{"v":1.176781591607638,"d":"1.18"},{"v":1.1599208883780876,"d":"1.16"},{"v":1.140793801101474,"d":"1.14"},{"v":1.1186009715450154,"d":"1.12"},{"v":1.0921793041844183,"d":"1.09"},{"v":1.059759791977284,"d":"1.06"},{"v":1.0185055292319245,"d":"1.02"},{"v":0.9635545551109574,"d":"0.96"},{"v":0.885811583481515,"d":"0.89"},{"v":0.7660444431189773,"d":"0.77"},{"v":0.5552682576204588,"d":"0.56"},{"v":0.08075322178617093,"d":"0.08"},{"v":2.0164331368355133,"d":"2.02"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":37.0150115351941,"d":"37.02"},{"v":107.52247001206348,"d":"107.52"},{"v":183.69209801942404,"d":"183.69"},{"v":261.45054428755213,"d":"261.45"},{"v":337.01791737288306,"d":"337.02"},{"v":407.5197330526234,"d":"407.52"},{"v":471.19318173538505,"d":"471.19"},{"v":527.2714576242289,"d":"527.27"},{"v":575.7162242606579,"d":"575.72"},{"v":616.9364363986165,"d":"616.94"},{"v":651.5629472410801,"d":"651.56"},{"v":680.2949550519771,"d":"680.29"},{"v":703.8078525738484,"d":"703.81"},{"v":722.7046122991308,"d":"722.70"},{"v":737.4944669267458,"d":"737.49"},{"v":748.5869519235048,"d":"748.59"},{"v":756.2934960947003,"d":"756.29"},{"v":760.8318204820407,"d":"760.83"},{"v":762.3304402000456,"d":"762.33"},{"v":760.8318204820407,"d":"760.83"},{"v":756.2934960947003,"d":"756.29"},{"v":748.5869519235048,"d":"748.59"},{"v":737.4944669267458,"d":"737.49"},{"v":722.7046122991308,"d":"722.70"},{"v":703.8078525738484,"d":"703.81"},{"v":680.2949550519771,"d":"680.29"},{"v":651.5629472410801,"d":"651.56"},{"v":616.9364363986165,"d":"616.94"},{"v":575.7162242606579,"d":"575.72"},{"v":527.2714576242289,"d":"527.27"},{"v":471.19318173538505,"d":"471.19"},{"v":407.5197330526234,"d":"407.52"},{"v":337.01791737288306,"d":"337.02"},{"v":261.45054428755213,"d":"261.45"},{"v":183.69209801942404,"d":"183.69"},{"v":107.52247001206348,"d":"107.52"},{"v":37.0150115351941,"d":"37.02"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"},{"v":-9.993726614739302e-14,"d":"-0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":18.369839067699157,"d":"18.37"},{"v":49.47947532704032,"d":"49.48"},{"v":79.06191494880149,"d":"79.06"},{"v":106.22023011513953,"d":"106.22"},{"v":130.40895265132224,"d":"130.41"},{"v":151.4303619176855,"d":"151.43"},{"v":169.35781308512438,"d":"169.36"},{"v":184.43488120784113,"d":"184.43"},{"v":196.98587899614853,"d":"196.99"},{"v":207.35238125331438,"d":"207.35"},{"v":215.8555776991777,"d":"215.86"},{"v":222.7780168429074,"d":"222.78"},{"v":228.3576070325877,"d":"228.36"},{"v":232.7883096812018,"d":"232.79"},{"v":236.22387164444874,"d":"236.22"},{"v":238.782461779983,"d":"238.78"},{"v":240.55108125967521,"d":"240.55"},{"v":241.58920963537065,"d":"241.59"},{"v":241.93146533513814,"d":"241.93"},{"v":241.58920963537065,"d":"241.59"},{"v":240.55108125967521,"d":"240.55"},{"v":238.782461779983,"d":"238.78"},{"v":236.22387164444874,"d":"236.22"},{"v":232.7883096812018,"d":"232.79"},{"v":228.3576070325877,"d":"228.36"},{"v":222.7780168429074,"d":"222.78"},{"v":215.8555776991777,"d":"215.86"},{"v":207.35238125331438,"d":"207.35"},{"v":196.98587899614853,"d":"196.99"},{"v":184.43488120784113,"d":"184.43"},{"v":169.35781308512438,"d":"169.36"},{"v":151.4303619176855,"d":"151.43"},{"v":130.40895265132224,"d":"130.41"},{"v":106.22023011513953,"d":"106.22"},{"v":79.06191494880149,"d":"79.06"},{"v":49.47947532704032,"d":"49.48"},{"v":18.369839067699157,"d":"18.37"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"},{"v":-5.200618638961138e-14,"d":"-0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":254.59395555982513,"d":"254.59"},{"v":321.11953891615843,"d":"321.12"},{"v":383.40701162126174,"d":"383.41"},{"v":439.40618192477086,"d":"439.41"},{"v":488.16415815137316,"d":"488.16"},{"v":529.5349935460388,"d":"529.53"},{"v":563.8703805547572,"d":"563.87"},{"v":591.7715106354153,"d":"591.77"},{"v":613.9206064806148,"d":"613.92"},{"v":630.9803962435927,"d":"630.98"},{"v":643.5415060587923,"d":"643.54"},{"v":652.099717601968,"d":"652.10"},{"v":657.0499571088568,"d":"657.05"},{"v":658.6885225370202,"d":"658.69"},{"v":657.2184895536118,"d":"657.22"},{"v":652.755500172874,"d":"652.76"},{"v":645.3325428379137,"d":"645.33"},{"v":634.9032011943552,"d":"634.90"},{"v":621.3434415629279,"d":"621.34"},{"v":604.4525330627035,"d":"604.45"},{"v":583.9543316308142,"d":"583.95"},{"v":559.5010966782871,"d":"559.50"},{"v":530.6834534154867,"d":"530.68"},{"v":497.0522662676314,"d":"497.05"},{"v":458.1611220148821,"d":"458.16"},{"v":413.6414449645164,"d":"413.64"},{"v":363.32441890523535,"d":"363.32"},{"v":307.42099188804673,"d":"307.42"},{"v":246.75608007256994,"d":"246.76"},{"v":183.01661420148227,"d":"183.02"},{"v":118.9133195753897,"d":"118.91"},{"v":58.09781944813421,"d":"58.10"},{"v":4.687158822933216,"d":"4.69"},{"v":37.596743605469975,"d":"37.60"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":93.79482357083064,"d":"93.79"},{"v":115.15400308141677,"d":"115.15"},{"v":133.7163745921121,"d":"133.72"},{"v":149.5467123488832,"d":"149.55"},{"v":162.8600985372083,"d":"162.86"},{"v":173.94290848702775,"d":"173.94"},{"v":183.0967603399518,"d":"183.10"},{"v":190.60527175593478,"d":"190.61"},{"v":196.71793934724133,"d":"196.72"},{"v":201.64484147192437,"d":"201.64"},{"v":205.55725036777312,"d":"205.56"},{"v":208.5909279248647,"d":"208.59"},{"v":210.85021987040437,"d":"210.85"},{"v":212.41195017245556,"d":"212.41"},{"v":213.3286405970261,"d":"213.33"},{"v":213.63085998537616,"d":"213.63"},{"v":213.3286405970261,"d":"213.33"},{"v":212.41195017245556,"d":"212.41"},{"v":210.85021987040437,"d":"210.85"},{"v":208.5909279248647,"d":"208.59"},{"v":205.55725036777312,"d":"205.56"},{"v":201.64484147192437,"d":"201.64"},{"v":196.71793934724133,"d":"196.72"},{"v":190.60527175593478,"d":"190.61"},{"v":183.0967603399518,"d":"183.10"},{"v":173.94290848702775,"d":"173.94"},{"v":162.8600985372083,"d":"162.86"},{"v":149.5467123488832,"d":"149.55"},{"v":133.7163745921121,"d":"133.72"},{"v":115.15400308141677,"d":"115.15"},{"v":93.79482357083064,"d":"93.79"},{"v":69.81342777883806,"d":"69.81"},{"v":43.691476224881065,"d":"43.69"},{"v":16.220976103250003,"d":"16.22"},{"v":-4.59226182405915e-14,"d":"-0.00"},{"v":-4.59226182405915e-14,"d":"-0.00"},{"v":-4.59226182405915e-14,"d":"-0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":348.3887791306558,"d":"348.39"},{"v":436.2735419975752,"d":"436.27"},{"v":517.1233862133738,"d":"517.12"},{"v":588.952894273654,"d":"588.95"},{"v":651.0242566885814,"d":"651.02"},{"v":703.4779020330666,"d":"703.48"},{"v":746.967140894709,"d":"746.97"},{"v":782.3767823913502,"d":"782.38"},{"v":810.6385458278561,"d":"810.64"},{"v":832.6252377155171,"d":"832.63"},{"v":849.0987564265654,"d":"849.10"},{"v":860.6906455268327,"d":"860.69"},{"v":867.9001769792612,"d":"867.90"},{"v":871.1004727094758,"d":"871.10"},{"v":870.5471301506379,"d":"870.55"},{"v":866.3863601582502,"d":"866.39"},{"v":858.6611834349399,"d":"858.66"},{"v":847.3151513668108,"d":"847.32"},{"v":832.1936614333322,"d":"832.19"},{"v":813.0434609875682,"d":"813.04"},{"v":789.5115819985873,"d":"789.51"},{"v":761.1459381502115,"d":"761.15"},{"v":727.401392762728,"d":"727.40"},{"v":687.6575380235662,"d":"687.66"},{"v":641.2578823548339,"d":"641.26"},{"v":587.5843534515441,"d":"587.58"},{"v":526.1845174424436,"d":"526.18"},{"v":456.96770423692993,"d":"456.97"},{"v":380.472454664682,"d":"380.47"},{"v":298.17061728289906,"d":"298.17"},{"v":212.70814314622035,"d":"212.71"},{"v":127.91124722697228,"d":"127.91"},{"v":48.37863504781428,"d":"48.38"},{"v":53.81771970871998,"d":"53.82"},{"v":-4.59226182405915e-14,"d":"-0.00"},{"v":-4.59226182405915e-14,"d":"-0.00"},{"v":-4.59226182405915e-14,"d":"-0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":254.59395555982513,"d":"254.59"},{"v":321.11953891615843,"d":"321.12"},{"v":383.40701162126174,"d":"383.41"},{"v":439.40618192477086,"d":"439.41"},{"v":488.16415815137316,"d":"488.16"},{"v":529.5349935460388,"d":"529.53"},{"v":563.8703805547572,"d":"563.87"},{"v":591.7715106354153,"d":"591.77"},{"v":613.9206064806148,"d":"613.92"},{"v":630.9803962435927,"d":"630.98"},{"v":643.5415060587923,"d":"643.54"},{"v":652.099717601968,"d":"652.10"},{"v":657.0499571088568,"d":"657.05"},{"v":658.6885225370202,"d":"658.69"},{"v":657.2184895536118,"d":"657.22"},{"v":652.755500172874,"d":"652.76"},{"v":645.3325428379137,"d":"645.33"},{"v":634.9032011943552,"d":"634.90"},{"v":621.3434415629279,"d":"621.34"},{"v":604.4525330627035,"d":"604.45"},{"v":583.9543316308142,"d":"583.95"},{"v":559.5010966782871,"d":"559.50"},{"v":530.6834534154867,"d":"530.68"},{"v":497.0522662676314,"d":"497.05"},{"v":458.1611220148821,"d":"458.16"},{"v":413.6414449645164,"d":"413.64"},{"v":363.32441890523535,"d":"363.32"},{"v":307.42099188804673,"d":"307.42"},{"v":246.75608007256994,"d":"246.76"},{"v":183.01661420148227,"d":"183.02"},{"v":118.9133195753897,"d":"118.91"},{"v":58.09781944813421,"d":"58.10"},{"v":4.687158822933216,"d":"4.69"},{"v":37.596743605469975,"d":"37.60"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":348.3887791306558,"d":"348.39"},{"v":436.2735419975752,"d":"436.27"},{"v":517.1233862133738,"d":"517.12"},{"v":588.952894273654,"d":"588.95"},{"v":651.0242566885814,"d":"651.02"},{"v":703.4779020330666,"d":"703.48"},{"v":746.967140894709,"d":"746.97"},{"v":782.3767823913502,"d":"782.38"},{"v":810.6385458278561,"d":"810.64"},{"v":832.6252377155171,"d":"832.63"},{"v":849.0987564265654,"d":"849.10"},{"v":860.6906455268327,"d":"860.69"},{"v":867.9001769792612,"d":"867.90"},{"v":871.1004727094758,"d":"871.10"},{"v":870.5471301506379,"d":"870.55"},{"v":866.3863601582502,"d":"866.39"},{"v":858.6611834349399,"d":"858.66"},{"v":847.3151513668108,"d":"847.32"},{"v":832.1936614333322,"d":"832.19"},{"v":813.0434609875682,"d":"813.04"},{"v":789.5115819985873,"d":"789.51"},{"v":761.1459381502115,"d":"761.15"},{"v":727.401392762728,"d":"727.40"},{"v":687.6575380235662,"d":"687.66"},{"v":641.2578823548339,"d":"641.26"},{"v":587.5843534515441,"d":"587.58"},{"v":526.1845174424436,"d":"526.18"},{"v":456.96770423692993,"d":"456.97"},{"v":380.472454664682,"d":"380.47"},{"v":298.17061728289906,"d":"298.17"},{"v":212.70814314622035,"d":"212.71"},{"v":127.91124722697228,"d":"127.91"},{"v":48.37863504781428,"d":"48.38"},{"v":53.81771970871998,"d":"53.82"},{"v":-4.59226182405915e-14,"d":"-0.00"},{"v":-4.59226182405915e-14,"d":"-0.00"},{"v":-4.59226182405915e-14,"d":"-0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":15606.961006815707,"d":"15,607"},"W/m2"]
[null,"Total Directa disponible",{"v":15606.961006815707,"d":"15,607"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":21253.955191838173,"d":"21,254"}]
[null,"Total global ",{"v":21253.955191838173,"d":"21,254"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.26569145055838805,"d":"0.266"},{"v":0.34371547018839144,"d":"0.344"}]
[]
[null,"OCTUBRE"]
[null,"Declinacion dia tipo",{"v":-9.78318998125884,"d":"-9.78"},{"v":-0.17074887652108908,"d":"-0.17"}]
[null,"ocaso",{"v":-81.56150716812043,"d":"-81.56"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"},{"v":0.22025756344193012,"d":"0.220"}]
[null,"c",{"v":-0.5510676573382294,"d":"-0.551"},{"v":-0.5466623569682525,"d":"-0.547"},{"v":-0.5335803086808737,"d":"-0.534"},{"v":-0.5122190038934694,"d":"-0.512"},{"v":-0.4832274950426632,"d":"-0.483"},{"v":-0.4474866744544754,"d":"-0.447"},{"v":-0.4060825088767501,"d":"-0.406"},{"v":-0.36027304292904755,"d":"-0.360"},{"v":-0.311450174053481,"d":"-0.311"},{"v":-0.26109736041527065,"d":"-0.261"},{"v":-0.2107445467770602,"d":"-0.211"},{"v":-0.16192167790149345,"d":"-0.162"},{"v":-0.11611221195379118,"d":"-0.116"},{"v":-0.07470804637606593,"d":"-0.075"},{"v":-0.038967225787878056,"d":"-0.039"},{"v":-0.009975716937071812,"d":"-0.010"},{"v":0.011385587850332432,"d":"0.011"},{"v":0.02446763613771108,"d":"0.024"},{"v":0.02887293650768804,"d":"0.029"},{"v":0.02446763613771109,"d":"0.024"},{"v":0.011385587850332411,"d":"0.011"},{"v":-0.009975716937071777,"d":"-0.010"},{"v":-0.0389672257878781,"d":"-0.039"},{"v":-0.07470804637606598,"d":"-0.075"},{"v":-0.11611221195379137,"d":"-0.116"},{"v":-0.16192167790149367,"d":"-0.162"},{"v":-0.2107445467770602,"d":"-0.211"},{"v":-0.26109736041527076,"d":"-0.261"},{"v":-0.3114501740534812,"d":"-0.311"},{"v":-0.36027304292904777,"d":"-0.360"},{"v":-0.4060825088767501,"d":"-0.406"},{"v":-0.4474866744544754,"d":"-0.447"},{"v":-0.4832274950426633,"d":"-0.483"},{"v":-0.5122190038934696,"d":"-0.512"},{"v":-0.5335803086808737,"d":"-0.534"},{"v":-0.5466623569682525,"d":"-0.547"},{"v":-0.5510676573382294,"d":"-0.551"},{"v":-0.5466623569682525,"d":"-0.547"},{"v":-0.5335803086808737,"d":"-0.534"},{"v":-0.5122190038934696,"d":"-0.512"},{"v":-0.4832274950426633,"d":"-0.483"},{"v":-0.4474866744544754,"d":"-0.447"},{"v":-0.4060825088767501,"d":"-0.406"},{"v":-0.36027304292904777,"d":"-0.360"},{"v":-0.3114501740534812,"d":"-0.311"},{"v":-0.26109736041527076,"d":"-0.261"},{"v":-0.2107445467770602,"d":"-0.211"},{"v":-0.16192167790149367,"d":"-0.162"},{"v":-0.11611221195379137,"d":"-0.116"},{"v":-0.07470804637606598,"d":"-0.075"},{"v":-0.0389672257878781,"d":"-0.039"},{"v":-0.009975716937071777,"d":"-0.010"},{"v":0.011385587850332411,"d":"0.011"},{"v":0.02446763613771109,"d":"0.024"},{"v":0.02887293650768804,"d":"0.029"},{"v":0.02446763613771108,"d":"0.024"},{"v":0.011385587850332432,"d":"0.011"},{"v":-0.009975716937071812,"d":"-0.010"},{"v":-0.038967225787878056,"d":"-0.039"},{"v":-0.07470804637606593,"d":"-0.075"},{"v":-0.11611221195379118,"d":"-0.116"},{"v":-0.16192167790149345,"d":"-0.162"},{"v":-0.2107445467770602,"d":"-0.211"},{"v":-0.26109736041527065,"d":"-0.261"},{"v":-0.311450174053481,"d":"-0.311"},{"v":-0.36027304292904755,"d":"-0.360"},{"v":-0.4060825088767501,"d":"-0.406"},{"v":-0.4474866744544754,"d":"-0.447"},{"v":-0.4832274950426632,"d":"-0.483"},{"v":-0.5122190038934694,"d":"-0.512"},{"v":-0.5335803086808737,"d":"-0.534"},{"v":-0.5466623569682525,"d":"-0.547"},{"v":-0.5510676573382294,"d":"-0.551"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-3.353009965282397,"d":"-3.35"},{"v":2.388371086226928,"d":"2.39"},{"v":7.814483839261907,"d":"7.81"},{"v":12.827019688609882,"d":"12.83"},{"v":17.3695331324303,"d":"17.37"},{"v":21.42112721099272,"d":"21.42"},{"v":24.98677485473458,"d":"24.99"},{"v":28.087710457208406,"d":"28.09"},{"v":30.75363037091365,"d":"30.75"},{"v":33.01712731272384,"d":"33.02"},{"v":34.910092433620434,"d":"34.91"},{"v":36.461590907144405,"d":"36.46"},{"v":37.69673077559649,"d":"37.70"},{"v":38.63614637157082,"d":"38.64"},{"v":39.29582874110849,"d":"39.30"},{"v":39.68712687653459,"d":"39.69"},{"v":39.816810018741165,"d":"39.82"},{"v":39.68712687653459,"d":"39.69"},{"v":39.29582874110849,"d":"39.30"},{"v":38.63614637157082,"d":"38.64"},{"v":37.69673077559649,"d":"37.70"},{"v":36.461590907144405,"d":"36.46"},{"v":34.910092433620434,"d":"34.91"},{"v":33.01712731272384,"d":"33.02"},{"v":30.75363037091365,"d":"30.75"},{"v":28.087710457208406,"d":"28.09"},{"v":24.98677485473458,"d":"24.99"},{"v":21.42112721099272,"d":"21.42"},{"v":17.3695331324303,"d":"17.37"},{"v":12.827019688609882,"d":"12.83"},{"v":7.814483839261907,"d":"7.81"},{"v":2.388371086226928,"d":"2.39"},{"v":-3.353009965282397,"d":"-3.35"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",288.5]
[null,"Declinacion . radianes",{"v":-0.17074887652108908,"d":"-0.171"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.4235168429726577,"d":"1.424"}]
[null,"Distancia sol - tierra. Bo",{"v":1.0328761111001858,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":0.5855691384778763,"d":"0.586"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":6316.206152618009,"d":"6,316"}]
[null,"H1",{"v":37906.83551716839,"d":"37,907"}]
[null,"H2",{"v":0.7423393141537294,"d":"0.742"}]
[null,"H3",{"v":-0.1567701756758531,"d":"-0.157"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":3565.1422222222222,"d":"3,565"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.5644436131560563,"d":"0.564"}]
[null,"Fraccion difusa diaria promedio",{"v":0.35851676700513174,"d":"0.359"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.5933379102280565,"d":"0.593"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.48571283531556114,"d":"0.486"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-3.353009965282397,"d":"-3.35"},{"v":2.388371086226928,"d":"2.39"},{"v":7.814483839261907,"d":"7.81"},{"v":12.827019688609882,"d":"12.83"},{"v":17.3695331324303,"d":"17.37"},{"v":21.42112721099272,"d":"21.42"},{"v":24.98677485473458,"d":"24.99"},{"v":28.087710457208406,"d":"28.09"},{"v":30.75363037091365,"d":"30.75"},{"v":33.01712731272384,"d":"33.02"},{"v":34.910092433620434,"d":"34.91"},{"v":36.461590907144405,"d":"36.46"},{"v":37.69673077559649,"d":"37.70"},{"v":38.63614637157082,"d":"38.64"},{"v":39.29582874110849,"d":"39.30"},{"v":39.68712687653459,"d":"39.69"},{"v":39.816810018741165,"d":"39.82"},{"v":39.68712687653459,"d":"39.69"},{"v":39.29582874110849,"d":"39.30"},{"v":38.63614637157082,"d":"38.64"},{"v":37.69673077559649,"d":"37.70"},{"v":36.461590907144405,"d":"36.46"},{"v":34.910092433620434,"d":"34.91"},{"v":33.01712731272384,"d":"33.02"},{"v":30.75363037091365,"d":"30.75"},{"v":28.087710457208406,"d":"28.09"},{"v":24.98677485473458,"d":"24.99"},{"v":21.42112721099272,"d":"21.42"},{"v":17.3695331324303,"d":"17.37"},{"v":12.827019688609882,"d":"12.83"},{"v":7.814483839261907,"d":"7.81"},{"v":2.388371086226928,"d":"2.39"},{"v":-3.353009965282397,"d":"-3.35"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":81.56150716812043,"d":"81.56"},{"v":86.05422970791672,"d":"86.05"},{"v":78.32985095634594,"d":"78.33"},{"v":70.85720591530513,"d":"70.86"},{"v":63.731659000288516,"d":"63.73"},{"v":57.00635351606991,"d":"57.01"},{"v":50.698085635451434,"d":"50.70"},{"v":44.79667985175741,"d":"44.80"},{"v":39.27439883929154,"d":"39.27"},{"v":34.09360383777497,"d":"34.09"},{"v":29.212200693954614,"d":"29.21"},{"v":24.58710865646319,"d":"24.59"},{"v":20.1762265762749,"d":"20.18"},{"v":15.939363911311561,"d":"15.94"},{"v":11.838506224574918,"d":"11.84"},{"v":7.837675832780905,"d":"7.84"},{"v":3.9025582179580174,"d":"3.90"},{"v":0,"d":"0.00"},{"v":-3.9025582179580174,"d":"-3.90"},{"v":-7.837675832780905,"d":"-7.84"},{"v":-11.838506224574918,"d":"-11.84"},{"v":-15.939363911311561,"d":"-15.94"},{"v":-20.1762265762749,"d":"-20.18"},{"v":-24.58710865646319,"d":"-24.59"},{"v":-29.212200693954614,"d":"-29.21"},{"v":-34.09360383777497,"d":"-34.09"},{"v":-39.27439883929154,"d":"-39.27"},{"v":-44.79667985175741,"d":"-44.80"},{"v":-50.698085635451434,"d":"-50.70"},{"v":-57.00635351606991,"d":"-57.01"},{"v":-63.731659000288516,"d":"-63.73"},{"v":-70.85720591530513,"d":"-70.86"},{"v":-78.32985095634594,"d":"-78.33"},{"v":-86.05422970791672,"d":"-86.05"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"},{"v":-81.56150716812043,"d":"-81.56"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":3.870638177209914,"d":"3.87"},{"v":-8.471648298609564,"d":"-8.47"},{"v":-3.4524804191646785,"d":"-3.45"},{"v":-2.5806835545354376,"d":"-2.58"},{"v":-2.219125147663159,"d":"-2.22"},{"v":-2.0211485327379384,"d":"-2.02"},{"v":-1.8958956132530451,"d":"-1.90"},{"v":-1.8091338787738833,"d":"-1.81"},{"v":-1.7451043250229252,"d":"-1.75"},{"v":-1.6955495307980173,"d":"-1.70"},{"v":-1.6557284263404932,"d":"-1.66"},{"v":-1.6227253403037118,"d":"-1.62"},{"v":-1.5946473803430643,"d":"-1.59"},{"v":-1.5702095401239418,"d":"-1.57"},{"v":-1.5485052263152876,"d":"-1.55"},{"v":-1.528872062119367,"d":"-1.53"},{"v":-1.510809527805909,"d":"-1.51"},{"v":-1.4939260853113945,"d":"-1.49"},{"v":-1.4779035829236973,"d":"-1.48"},{"v":-1.4624718459620538,"d":"-1.46"},{"v":-1.447388954619744,"d":"-1.45"},{"v":-1.4324238850022006,"d":"-1.43"},{"v":-1.417338321517384,"d":"-1.42"},{"v":-1.4018633697388243,"d":"-1.40"},{"v":-1.385663612311919,"d":"-1.39"},{"v":-1.3682724095831926,"d":"-1.37"},{"v":-1.3489591057591865,"d":"-1.35"},{"v":-1.326417779778556,"d":"-1.33"},{"v":-1.2979088947311386,"d":"-1.30"},{"v":-1.2562666721601874,"d":"-1.26"},{"v":-1.174252151800012,"d":"-1.17"},{"v":-0.7660444431189777,"d":"-0.77"},{"v":-1.7222584883792091,"d":"-1.72"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":3.870638177209914,"d":"3.87"},{"v":8.471648298609564,"d":"8.47"},{"v":3.4524804191646785,"d":"3.45"},{"v":2.5806835545354376,"d":"2.58"},{"v":2.219125147663159,"d":"2.22"},{"v":2.0211485327379384,"d":"2.02"},{"v":1.8958956132530451,"d":"1.90"},{"v":1.8091338787738833,"d":"1.81"},{"v":1.7451043250229252,"d":"1.75"},{"v":1.6955495307980173,"d":"1.70"},{"v":1.6557284263404932,"d":"1.66"},{"v":1.6227253403037118,"d":"1.62"},{"v":1.5946473803430643,"d":"1.59"},{"v":1.5702095401239418,"d":"1.57"},{"v":1.5485052263152876,"d":"1.55"},{"v":1.528872062119367,"d":"1.53"},{"v":1.510809527805909,"d":"1.51"},{"v":1.4939260853113945,"d":"1.49"},{"v":1.4779035829236973,"d":"1.48"},{"v":1.4624718459620538,"d":"1.46"},{"v":1.447388954619744,"d":"1.45"},{"v":1.4324238850022006,"d":"1.43"},{"v":1.417338321517384,"d":"1.42"},{"v":1.4018633697388243,"d":"1.40"},{"v":1.385663612311919,"d":"1.39"},{"v":1.3682724095831926,"d":"1.37"},{"v":1.3489591057591865,"d":"1.35"},{"v":1.326417779778556,"d":"1.33"},{"v":1.2979088947311386,"d":"1.30"},{"v":1.2562666721601874,"d":"1.26"},{"v":1.174252151800012,"d":"1.17"},{"v":0.7660444431189777,"d":"0.77"},{"v":1.7222584883792091,"d":"1.72"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-29.21483962969426,"d":"-29.21"},{"v":22.96874169509323,"d":"22.97"},{"v":81.55307441685956,"d":"81.55"},{"v":143.01467077776152,"d":"143.01"},{"v":204.09475011131934,"d":"204.09"},{"v":262.2483342043253,"d":"262.25"},{"v":315.77362154653457,"d":"315.77"},{"v":363.7228275936149,"d":"363.72"},{"v":405.7180594267878,"d":"405.72"},{"v":441.7586904554487,"d":"441.76"},{"v":472.06163004792796,"d":"472.06"},{"v":496.945002756354,"d":"496.95"},{"v":516.7506095602487,"d":"516.75"},{"v":531.7957004564183,"d":"531.80"},{"v":542.3447740996554,"d":"542.34"},{"v":548.5940847799687,"d":"548.59"},{"v":550.6637320905637,"d":"550.66"},{"v":548.5940847799687,"d":"548.59"},{"v":542.3447740996554,"d":"542.34"},{"v":531.7957004564183,"d":"531.80"},{"v":516.7506095602487,"d":"516.75"},{"v":496.945002756354,"d":"496.95"},{"v":472.06163004792796,"d":"472.06"},{"v":441.7586904554487,"d":"441.76"},{"v":405.7180594267878,"d":"405.72"},{"v":363.7228275936149,"d":"363.72"},{"v":315.77362154653457,"d":"315.77"},{"v":262.2483342043253,"d":"262.25"},{"v":204.09475011131934,"d":"204.09"},{"v":143.01467077776152,"d":"143.01"},{"v":81.55307441685956,"d":"81.55"},{"v":22.96874169509323,"d":"22.97"},{"v":-29.21483962969426,"d":"-29.21"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-16.711332353769663,"d":"-16.71"},{"v":11.906940221888384,"d":"11.91"},{"v":38.84876051183684,"d":"38.85"},{"v":63.43311877668824,"d":"63.43"},{"v":85.2981506677232,"d":"85.30"},{"v":104.35215573544649,"d":"104.35"},{"v":120.69242155195417,"d":"120.69"},{"v":134.5253526344492,"d":"134.53"},{"v":146.10428459210655,"d":"146.10"},{"v":155.68809008479022,"d":"155.69"},{"v":163.51710547489853,"d":"163.52"},{"v":169.80116124059572,"d":"169.80"},{"v":174.71507683959325,"d":"174.72"},{"v":178.3982368245694,"d":"178.40"},{"v":180.95604438361931,"d":"180.96"},{"v":182.4619244392129,"d":"182.46"},{"v":182.95912564948844,"d":"182.96"},{"v":182.4619244392129,"d":"182.46"},{"v":180.95604438361931,"d":"180.96"},{"v":178.3982368245694,"d":"178.40"},{"v":174.71507683959325,"d":"174.72"},{"v":169.80116124059572,"d":"169.80"},{"v":163.51710547489853,"d":"163.52"},{"v":155.68809008479022,"d":"155.69"},{"v":146.10428459210655,"d":"146.10"},{"v":134.5253526344492,"d":"134.53"},{"v":120.69242155195417,"d":"120.69"},{"v":104.35215573544649,"d":"104.35"},{"v":85.2981506677232,"d":"85.30"},{"v":63.43311877668824,"d":"63.43"},{"v":38.84876051183684,"d":"38.85"},{"v":11.906940221888384,"d":"11.91"},{"v":-16.711332353769663,"d":"-16.71"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":93.71169163003259,"d":"93.71"},{"v":147.43580757095285,"d":"147.44"},{"v":205.37480249357657,"d":"205.37"},{"v":263.6245212821514,"d":"263.62"},{"v":319.1316294373021,"d":"319.13"},{"v":369.85359129786497,"d":"369.85"},{"v":414.64891687805545,"d":"414.65"},{"v":453.0531212995302,"d":"453.05"},{"v":485.046872233577,"d":"485.05"},{"v":510.86594012727767,"d":"510.87"},{"v":530.8646015519224,"d":"530.86"},{"v":545.4260662372376,"d":"545.43"},{"v":554.9080688503329,"d":"554.91"},{"v":559.6123366967248,"d":"559.61"},{"v":559.7692309883901,"d":"559.77"},{"v":555.5316228292985,"d":"555.53"},{"v":546.9743850044691,"d":"546.97"},{"v":534.0976984755733,"d":"534.10"},{"v":516.8338409959779,"d":"516.83"},{"v":495.05845214735666,"d":"495.06"},{"v":468.6086524185466,"d":"468.61"},{"v":437.3119785717168,"d":"437.31"},{"v":401.0318958188198,"d":"401.03"},{"v":359.7373610433577,"d":"359.74"},{"v":313.6045813327611,"d":"313.60"},{"v":263.1565610951182,"d":"263.16"},{"v":209.43629848020885,"d":"209.44"},{"v":154.18716308165565,"d":"154.19"},{"v":99.97565149773122,"d":"99.98"},{"v":50.14563249411609,"d":"50.15"},{"v":8.473831549433893,"d":"8.47"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":10.514092806707914,"d":"10.51"},{"v":34.30431881199472,"d":"34.30"},{"v":56.01285346263818,"d":"56.01"},{"v":75.32016249752895,"d":"75.32"},{"v":92.14527238203573,"d":"92.15"},{"v":106.57409020420091,"d":"106.57"},{"v":118.78887573934499,"d":"118.79"},{"v":129.01332995988173,"d":"129.01"},{"v":137.4760431770253,"d":"137.48"},{"v":144.38923773942219,"d":"144.39"},{"v":149.93819862205183,"d":"149.94"},{"v":154.27729529083445,"d":"154.28"},{"v":157.5296074031271,"d":"157.53"},{"v":159.788208316241,"d":"159.79"},{"v":161.11793386833338,"d":"161.12"},{"v":161.55697358559297,"d":"161.56"},{"v":161.11793386833338,"d":"161.12"},{"v":159.788208316241,"d":"159.79"},{"v":157.5296074031271,"d":"157.53"},{"v":154.27729529083445,"d":"154.28"},{"v":149.93819862205183,"d":"149.94"},{"v":144.38923773942219,"d":"144.39"},{"v":137.4760431770253,"d":"137.48"},{"v":129.01332995988173,"d":"129.01"},{"v":118.78887573934499,"d":"118.79"},{"v":106.57409020420091,"d":"106.57"},{"v":92.14527238203573,"d":"92.15"},{"v":75.32016249752895,"d":"75.32"},{"v":56.01285346263818,"d":"56.01"},{"v":34.30431881199472,"d":"34.30"},{"v":10.514092806707914,"d":"10.51"},{"v":-14.756477820244651,"d":"-14.76"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":104.2257844367405,"d":"104.23"},{"v":181.74012638294755,"d":"181.74"},{"v":261.38765595621476,"d":"261.39"},{"v":338.94468377968036,"d":"338.94"},{"v":411.2769018193378,"d":"411.28"},{"v":476.42768150206587,"d":"476.43"},{"v":533.4377926174004,"d":"533.44"},{"v":582.0664512594119,"d":"582.07"},{"v":622.5229154106023,"d":"622.52"},{"v":655.2551778666998,"d":"655.26"},{"v":680.8028001739742,"d":"680.80"},{"v":699.703361528072,"d":"699.70"},{"v":712.43767625346,"d":"712.44"},{"v":719.4005450129658,"d":"719.40"},{"v":720.8871648567234,"d":"720.89"},{"v":717.0885964148915,"d":"717.09"},{"v":708.0923188728025,"d":"708.09"},{"v":693.8859067918144,"d":"693.89"},{"v":674.363448399105,"d":"674.36"},{"v":649.3357474381911,"d":"649.34"},{"v":618.5468510405984,"d":"618.55"},{"v":581.701216311139,"d":"581.70"},{"v":538.507938995845,"d":"538.51"},{"v":488.7506910032394,"d":"488.75"},{"v":432.39345707210606,"d":"432.39"},{"v":369.7306512993191,"d":"369.73"},{"v":301.5815708622446,"d":"301.58"},{"v":229.50732557918462,"d":"229.51"},{"v":155.9885049603694,"d":"155.99"},{"v":84.44995130611082,"d":"84.45"},{"v":18.987924356141807,"d":"18.99"},{"v":-14.756477820244651,"d":"-14.76"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":93.71169163003259,"d":"93.71"},{"v":147.43580757095285,"d":"147.44"},{"v":205.37480249357657,"d":"205.37"},{"v":263.6245212821514,"d":"263.62"},{"v":319.1316294373021,"d":"319.13"},{"v":369.85359129786497,"d":"369.85"},{"v":414.64891687805545,"d":"414.65"},{"v":453.0531212995302,"d":"453.05"},{"v":485.046872233577,"d":"485.05"},{"v":510.86594012727767,"d":"510.87"},{"v":530.8646015519224,"d":"530.86"},{"v":545.4260662372376,"d":"545.43"},{"v":554.9080688503329,"d":"554.91"},{"v":559.6123366967248,"d":"559.61"},{"v":559.7692309883901,"d":"559.77"},{"v":555.5316228292985,"d":"555.53"},{"v":546.9743850044691,"d":"546.97"},{"v":534.0976984755733,"d":"534.10"},{"v":516.8338409959779,"d":"516.83"},{"v":495.05845214735666,"d":"495.06"},{"v":468.6086524185466,"d":"468.61"},{"v":437.3119785717168,"d":"437.31"},{"v":401.0318958188198,"d":"401.03"},{"v":359.7373610433577,"d":"359.74"},{"v":313.6045813327611,"d":"313.60"},{"v":263.1565610951182,"d":"263.16"},{"v":209.43629848020885,"d":"209.44"},{"v":154.18716308165565,"d":"154.19"},{"v":99.97565149773122,"d":"99.98"},{"v":50.14563249411609,"d":"50.15"},{"v":8.473831549433893,"d":"8.47"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":104.2257844367405,"d":"104.23"},{"v":181.74012638294755,"d":"181.74"},{"v":261.38765595621476,"d":"261.39"},{"v":338.94468377968036,"d":"338.94"},{"v":411.2769018193378,"d":"411.28"},{"v":476.42768150206587,"d":"476.43"},{"v":533.4377926174004,"d":"533.44"},{"v":582.0664512594119,"d":"582.07"},{"v":622.5229154106023,"d":"622.52"},{"v":655.2551778666998,"d":"655.26"},{"v":680.8028001739742,"d":"680.80"},{"v":699.703361528072,"d":"699.70"},{"v":712.43767625346,"d":"712.44"},{"v":719.4005450129658,"d":"719.40"},{"v":720.8871648567234,"d":"720.89"},{"v":717.0885964148915,"d":"717.09"},{"v":708.0923188728025,"d":"708.09"},{"v":693.8859067918144,"d":"693.89"},{"v":674.363448399105,"d":"674.36"},{"v":649.3357474381911,"d":"649.34"},{"v":618.5468510405984,"d":"618.55"},{"v":581.701216311139,"d":"581.70"},{"v":538.507938995845,"d":"538.51"},{"v":488.7506910032394,"d":"488.75"},{"v":432.39345707210606,"d":"432.39"},{"v":369.7306512993191,"d":"369.73"},{"v":301.5815708622446,"d":"301.58"},{"v":229.50732557918462,"d":"229.51"},{"v":155.9885049603694,"d":"155.99"},{"v":84.44995130611082,"d":"84.45"},{"v":18.987924356141807,"d":"18.99"},{"v":-14.756477820244651,"d":"-14.76"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":11427.49280541107,"d":"11,427"},"W/m2"]
[null,"Total Directa disponible",{"v":11427.49280541107,"d":"11,427"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":14948.67234173916,"d":"14,949"}]
[null,"Total global ",{"v":14948.67234173916,"d":"14,949"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.23555132227337516,"d":"0.236"},{"v":0.35851676700513174,"d":"0.359"}]
[]
[null,"NOVIEMBRE"]
[null,"Declinacion dia tipo",{"v":-19.14781730640673,"d":"-19.15"},{"v":-0.33419245656714935,"d":"-0.33"}]
[null,"ocaso",{"v":-72.81224142315592,"d":"-72.81"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"},{"v":0.42517496453094594,"d":"0.425"}]
[null,"c",{"v":-0.4723523885733629,"d":"-0.472"},{"v":-0.46794708820338604,"d":"-0.468"},{"v":-0.45486503991600724,"d":"-0.455"},{"v":-0.43350373512860296,"d":"-0.434"},{"v":-0.4045122262777967,"d":"-0.405"},{"v":-0.36877140568960887,"d":"-0.369"},{"v":-0.3273672401118836,"d":"-0.327"},{"v":-0.28155777416418104,"d":"-0.282"},{"v":-0.2327349052886145,"d":"-0.233"},{"v":-0.18238209165040414,"d":"-0.182"},{"v":-0.13202927801219372,"d":"-0.132"},{"v":-0.08320640913662697,"d":"-0.083"},{"v":-0.0373969431889247,"d":"-0.037"},{"v":0.004007222388800566,"d":"0.004"},{"v":0.03974804297698843,"d":"0.040"},{"v":0.06873955182779468,"d":"0.069"},{"v":0.09010085661519893,"d":"0.090"},{"v":0.10318290490257756,"d":"0.103"},{"v":0.10758820527255453,"d":"0.108"},{"v":0.10318290490257757,"d":"0.103"},{"v":0.0901008566151989,"d":"0.090"},{"v":0.0687395518277947,"d":"0.069"},{"v":0.03974804297698839,"d":"0.040"},{"v":0.00400722238880051,"d":"0.004"},{"v":-0.03739694318892489,"d":"-0.037"},{"v":-0.08320640913662719,"d":"-0.083"},{"v":-0.13202927801219372,"d":"-0.132"},{"v":-0.18238209165040425,"d":"-0.182"},{"v":-0.23273490528861468,"d":"-0.233"},{"v":-0.28155777416418126,"d":"-0.282"},{"v":-0.3273672401118836,"d":"-0.327"},{"v":-0.36877140568960887,"d":"-0.369"},{"v":-0.4045122262777968,"d":"-0.405"},{"v":-0.4335037351286032,"d":"-0.434"},{"v":-0.45486503991600724,"d":"-0.455"},{"v":-0.46794708820338604,"d":"-0.468"},{"v":-0.4723523885733629,"d":"-0.472"},{"v":-0.46794708820338604,"d":"-0.468"},{"v":-0.45486503991600724,"d":"-0.455"},{"v":-0.4335037351286032,"d":"-0.434"},{"v":-0.4045122262777968,"d":"-0.405"},{"v":-0.36877140568960887,"d":"-0.369"},{"v":-0.3273672401118836,"d":"-0.327"},{"v":-0.28155777416418126,"d":"-0.282"},{"v":-0.23273490528861468,"d":"-0.233"},{"v":-0.18238209165040425,"d":"-0.182"},{"v":-0.13202927801219372,"d":"-0.132"},{"v":-0.08320640913662719,"d":"-0.083"},{"v":-0.03739694318892489,"d":"-0.037"},{"v":0.00400722238880051,"d":"0.004"},{"v":0.03974804297698839,"d":"0.040"},{"v":0.0687395518277947,"d":"0.069"},{"v":0.0901008566151989,"d":"0.090"},{"v":0.10318290490257757,"d":"0.103"},{"v":0.10758820527255453,"d":"0.108"},{"v":0.10318290490257756,"d":"0.103"},{"v":0.09010085661519893,"d":"0.090"},{"v":0.06873955182779468,"d":"0.069"},{"v":0.03974804297698843,"d":"0.040"},{"v":0.004007222388800566,"d":"0.004"},{"v":-0.0373969431889247,"d":"-0.037"},{"v":-0.08320640913662697,"d":"-0.083"},{"v":-0.13202927801219372,"d":"-0.132"},{"v":-0.18238209165040414,"d":"-0.182"},{"v":-0.2327349052886145,"d":"-0.233"},{"v":-0.28155777416418104,"d":"-0.282"},{"v":-0.3273672401118836,"d":"-0.327"},{"v":-0.36877140568960887,"d":"-0.369"},{"v":-0.4045122262777967,"d":"-0.405"},{"v":-0.43350373512860296,"d":"-0.434"},{"v":-0.45486503991600724,"d":"-0.455"},{"v":-0.46794708820338604,"d":"-0.468"},{"v":-0.4723523885733629,"d":"-0.472"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-6.113736232499352,"d":"-6.11"},{"v":-0.546432079034663,"d":"-0.55"},{"v":4.562539327254076,"d":"4.56"},{"v":9.163899501034559,"d":"9.16"},{"v":13.24387701233431,"d":"13.24"},{"v":16.8127161611689,"d":"16.81"},{"v":19.8946653415299,"d":"19.89"},{"v":22.520478631082277,"d":"22.52"},{"v":24.722351146022326,"d":"24.72"},{"v":26.530771497977486,"d":"26.53"},{"v":27.972716446318408,"d":"27.97"},{"v":29.070708718208113,"d":"29.07"},{"v":29.842388436320963,"d":"29.84"},{"v":30.300362551457667,"d":"30.30"},{"v":30.452182693593276,"d":"30.45"},{"v":30.300362551457667,"d":"30.30"},{"v":29.842388436320963,"d":"29.84"},{"v":29.070708718208113,"d":"29.07"},{"v":27.972716446318408,"d":"27.97"},{"v":26.530771497977486,"d":"26.53"},{"v":24.722351146022326,"d":"24.72"},{"v":22.520478631082277,"d":"22.52"},{"v":19.8946653415299,"d":"19.89"},{"v":16.8127161611689,"d":"16.81"},{"v":13.24387701233431,"d":"13.24"},{"v":9.163899501034559,"d":"9.16"},{"v":4.562539327254076,"d":"4.56"},{"v":-0.546432079034663,"d":"-0.55"},{"v":-6.113736232499352,"d":"-6.11"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",319]
[null,"Declinacion . radianes",{"v":-0.33419245656714935,"d":"-0.334"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.2708133485910726,"d":"1.271"}]
[null,"Distancia sol - tierra. Bo",{"v":1.0328485526815891,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":0.41711996413623026,"d":"0.417"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":4499.119260082218,"d":"4,499"}]
[null,"H1",{"v":38466.78346442215,"d":"38,467"}]
[null,"H2",{"v":0.6872789743425612,"d":"0.687"}]
[null,"H3",{"v":-0.270159010206331,"d":"-0.270"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":2433.51,"d":"2,434"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.5408858621710618,"d":"0.541"}]
[null,"Fraccion difusa diaria promedio",{"v":0.3496090690974937,"d":"0.350"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.5202332290790681,"d":"0.520"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.5551885161443546,"d":"0.555"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-6.113736232499352,"d":"-6.11"},{"v":-0.546432079034663,"d":"-0.55"},{"v":4.562539327254076,"d":"4.56"},{"v":9.163899501034559,"d":"9.16"},{"v":13.24387701233431,"d":"13.24"},{"v":16.8127161611689,"d":"16.81"},{"v":19.8946653415299,"d":"19.89"},{"v":22.520478631082277,"d":"22.52"},{"v":24.722351146022326,"d":"24.72"},{"v":26.530771497977486,"d":"26.53"},{"v":27.972716446318408,"d":"27.97"},{"v":29.070708718208113,"d":"29.07"},{"v":29.842388436320963,"d":"29.84"},{"v":30.300362551457667,"d":"30.30"},{"v":30.452182693593276,"d":"30.45"},{"v":30.300362551457667,"d":"30.30"},{"v":29.842388436320963,"d":"29.84"},{"v":29.070708718208113,"d":"29.07"},{"v":27.972716446318408,"d":"27.97"},{"v":26.530771497977486,"d":"26.53"},{"v":24.722351146022326,"d":"24.72"},{"v":22.520478631082277,"d":"22.52"},{"v":19.8946653415299,"d":"19.89"},{"v":16.8127161611689,"d":"16.81"},{"v":13.24387701233431,"d":"13.24"},{"v":9.163899501034559,"d":"9.16"},{"v":4.562539327254076,"d":"4.56"},{"v":-0.546432079034663,"d":"-0.55"},{"v":-6.113736232499352,"d":"-6.11"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":72.81224142315592,"d":"72.81"},{"v":81.52013411125554,"d":"81.52"},{"v":73.60562157235546,"d":"73.61"},{"v":66.04134587917835,"d":"66.04"},{"v":58.87681898782643,"d":"58.88"},{"v":52.123913150491745,"d":"52.12"},{"v":45.768154978524294,"d":"45.77"},{"v":39.77868668284051,"d":"39.78"},{"v":34.11575809562436,"d":"34.12"},{"v":28.73576697288269,"d":"28.74"},{"v":23.594331441645256,"d":"23.59"},{"v":18.647953767572748,"d":"18.65"},{"v":13.854747427964288,"d":"13.85"},{"v":9.17457406493784,"d":"9.17"},{"v":4.568825185371664,"d":"4.57"},{"v":0,"d":"0.00"},{"v":-4.568825185371664,"d":"-4.57"},{"v":-9.17457406493784,"d":"-9.17"},{"v":-13.854747427964288,"d":"-13.85"},{"v":-18.647953767572748,"d":"-18.65"},{"v":-23.594331441645256,"d":"-23.59"},{"v":-28.73576697288269,"d":"-28.74"},{"v":-34.11575809562436,"d":"-34.12"},{"v":-39.77868668284051,"d":"-39.78"},{"v":-45.768154978524294,"d":"-45.77"},{"v":-52.123913150491745,"d":"-52.12"},{"v":-58.87681898782643,"d":"-58.88"},{"v":-66.04134587917835,"d":"-66.04"},{"v":-73.60562157235546,"d":"-73.61"},{"v":-81.52013411125554,"d":"-81.52"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"},{"v":-72.81224142315592,"d":"-72.81"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.676044266905075,"d":"2.68"},{"v":42.555932937578575,"d":"42.56"},{"v":-6.461771564536544,"d":"-6.46"},{"v":-3.818422360991816,"d":"-3.82"},{"v":-3.003254821065141,"d":"-3.00"},{"v":-2.6083479402468996,"d":"-2.61"},{"v":-2.375826400634654,"d":"-2.38"},{"v":-2.2228114999162547,"d":"-2.22"},{"v":-2.1145596434514826,"d":"-2.11"},{"v":-2.0339848197772845,"d":"-2.03"},{"v":-1.9717365692317854,"d":"-1.97"},{"v":-1.9222964707530938,"d":"-1.92"},{"v":-1.882228304389071,"d":"-1.88"},{"v":-1.8493164079017588,"d":"-1.85"},{"v":-1.822112697219385,"d":"-1.82"},{"v":-1.7996905212464842,"d":"-1.80"},{"v":-1.7815147394089463,"d":"-1.78"},{"v":-1.7673880722273891,"d":"-1.77"},{"v":-1.7574622571068705,"d":"-1.76"},{"v":-1.7523269706218245,"d":"-1.75"},{"v":-1.7532260845412944,"d":"-1.75"},{"v":-1.762531798234812,"d":"-1.76"},{"v":-1.784829685506743,"d":"-1.78"},{"v":-1.8296988631147728,"d":"-1.83"},{"v":-1.920269678431092,"d":"-1.92"},{"v":-2.1288566693971216,"d":"-2.13"},{"v":-2.8508252625818225,"d":"-2.85"},{"v":10.937327419874235,"d":"10.94"},{"v":-0.24301424328373208,"d":"-0.24"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.676044266905075,"d":"2.68"},{"v":42.555932937578575,"d":"42.56"},{"v":6.461771564536544,"d":"6.46"},{"v":3.818422360991816,"d":"3.82"},{"v":3.003254821065141,"d":"3.00"},{"v":2.6083479402468996,"d":"2.61"},{"v":2.375826400634654,"d":"2.38"},{"v":2.2228114999162547,"d":"2.22"},{"v":2.1145596434514826,"d":"2.11"},{"v":2.0339848197772845,"d":"2.03"},{"v":1.9717365692317854,"d":"1.97"},{"v":1.9222964707530938,"d":"1.92"},{"v":1.882228304389071,"d":"1.88"},{"v":1.8493164079017588,"d":"1.85"},{"v":1.822112697219385,"d":"1.82"},{"v":1.7996905212464842,"d":"1.80"},{"v":1.7815147394089463,"d":"1.78"},{"v":1.7673880722273891,"d":"1.77"},{"v":1.7574622571068705,"d":"1.76"},{"v":1.7523269706218245,"d":"1.75"},{"v":1.7532260845412944,"d":"1.75"},{"v":1.762531798234812,"d":"1.76"},{"v":1.784829685506743,"d":"1.78"},{"v":1.8296988631147728,"d":"1.83"},{"v":1.920269678431092,"d":"1.92"},{"v":2.1288566693971216,"d":"2.13"},{"v":2.8508252625818225,"d":"2.85"},{"v":10.937327419874235,"d":"10.94"},{"v":0.24301424328373208,"d":"0.24"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-48.97119813185922,"d":"-48.97"},{"v":-4.930192771448854,"d":"-4.93"},{"v":45.29911859837302,"d":"45.30"},{"v":98.17385773408066,"d":"98.17"},{"v":150.6536929363715,"d":"150.65"},{"v":200.46018379623212,"d":"200.46"},{"v":246.07649165707898,"d":"246.08"},{"v":286.61351016014777,"d":"286.61"},{"v":321.6379924595945,"d":"321.64"},{"v":351.0144696245438,"d":"351.01"},{"v":374.7802952411716,"d":"374.78"},{"v":393.055426188294,"d":"393.06"},{"v":405.981300520815,"d":"405.98"},{"v":413.68162300031156,"d":"413.68"},{"v":416.23881280022306,"d":"416.24"},{"v":413.68162300031156,"d":"413.68"},{"v":405.981300520815,"d":"405.98"},{"v":393.055426188294,"d":"393.06"},{"v":374.7802952411716,"d":"374.78"},{"v":351.0144696245438,"d":"351.01"},{"v":321.6379924595945,"d":"321.64"},{"v":286.61351016014777,"d":"286.61"},{"v":246.07649165707898,"d":"246.08"},{"v":200.46018379623212,"d":"200.46"},{"v":150.6536929363715,"d":"150.65"},{"v":98.17385773408066,"d":"98.17"},{"v":45.29911859837302,"d":"45.30"},{"v":-4.930192771448854,"d":"-4.93"},{"v":-48.97119813185922,"d":"-48.97"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-28.434990780272283,"d":"-28.43"},{"v":-2.54624653503434,"d":"-2.55"},{"v":21.238233120105118,"d":"21.24"},{"v":42.52046235148067,"d":"42.52"},{"v":61.166225878935784,"d":"61.17"},{"v":77.2250544699073,"d":"77.23"},{"v":90.8542442783203,"d":"90.85"},{"v":102.26044966614427,"d":"102.26"},{"v":111.6605557976456,"d":"111.66"},{"v":119.25824601080598,"d":"119.26"},{"v":125.23150564710802,"d":"125.23"},{"v":129.72694963726795,"d":"129.73"},{"v":132.85798233125297,"d":"132.86"},{"v":134.70481883200884,"d":"134.70"},{"v":135.31515845915823,"d":"135.32"},{"v":134.70481883200884,"d":"134.70"},{"v":132.85798233125297,"d":"132.86"},{"v":129.72694963726795,"d":"129.73"},{"v":125.23150564710802,"d":"125.23"},{"v":119.25824601080598,"d":"119.26"},{"v":111.6605557976456,"d":"111.66"},{"v":102.26044966614427,"d":"102.26"},{"v":90.8542442783203,"d":"90.85"},{"v":77.2250544699073,"d":"77.23"},{"v":61.166225878935784,"d":"61.17"},{"v":42.52046235148067,"d":"42.52"},{"v":21.238233120105118,"d":"21.24"},{"v":-2.54624653503434,"d":"-2.55"},{"v":-28.434990780272283,"d":"-28.43"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":155.47594560104181,"d":"155.48"},{"v":212.50816939403848,"d":"212.51"},{"v":268.7536668651518,"d":"268.75"},{"v":321.4400957443796,"d":"321.44"},{"v":368.78111328829806,"d":"368.78"},{"v":409.782102910828,"d":"409.78"},{"v":444.00981360074695,"d":"444.01"},{"v":471.3886407192525,"d":"471.39"},{"v":492.0444742501436,"d":"492.04"},{"v":506.1954011228262,"d":"506.20"},{"v":514.0804400850561,"d":"514.08"},{"v":515.916381372438,"d":"515.92"},{"v":511.8745575241239,"d":"511.87"},{"v":502.07191010933104,"d":"502.07"},{"v":486.5732170309844,"d":"486.57"},{"v":465.40360853409317,"d":"465.40"},{"v":438.5725790182705,"d":"438.57"},{"v":406.1126812478153,"d":"406.11"},{"v":368.1379191208463,"d":"368.14"},{"v":324.92813122258707,"d":"324.93"},{"v":277.0452749726797,"d":"277.05"},{"v":225.4831760241785,"d":"225.48"},{"v":171.840069589995,"d":"171.84"},{"v":118.47810193484295,"d":"118.48"},{"v":68.59338016153426,"d":"68.59"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-25.108728728819617,"d":"-25.11"},{"v":-2.248392272004174,"d":"-2.25"},{"v":18.753831791713537,"d":"18.75"},{"v":37.54651312734107,"d":"37.55"},{"v":54.01113666002738,"d":"54.01"},{"v":68.1914391580701,"d":"68.19"},{"v":80.22631662075088,"d":"80.23"},{"v":90.29824944187101,"d":"90.30"},{"v":98.59875204100429,"d":"98.60"},{"v":105.30768133174995,"d":"105.31"},{"v":110.58220232574901,"d":"110.58"},{"v":114.55177926483628,"d":"114.55"},{"v":117.31655071005433,"d":"117.32"},{"v":118.94734837980893,"d":"118.95"},{"v":119.48629183328018,"d":"119.49"},{"v":118.94734837980893,"d":"118.95"},{"v":117.31655071005433,"d":"117.32"},{"v":114.55177926483628,"d":"114.55"},{"v":110.58220232574901,"d":"110.58"},{"v":105.30768133174995,"d":"105.31"},{"v":98.59875204100429,"d":"98.60"},{"v":90.29824944187101,"d":"90.30"},{"v":80.22631662075088,"d":"80.23"},{"v":68.1914391580701,"d":"68.19"},{"v":54.01113666002738,"d":"54.01"},{"v":37.54651312734107,"d":"37.55"},{"v":18.753831791713537,"d":"18.75"},{"v":-2.248392272004174,"d":"-2.25"},{"v":-25.108728728819617,"d":"-25.11"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-25.108728728819617,"d":"-25.11"},{"v":-2.248392272004174,"d":"-2.25"},{"v":174.22977739275535,"d":"174.23"},{"v":250.05468252137956,"d":"250.05"},{"v":322.76480352517916,"d":"322.76"},{"v":389.63153490244974,"d":"389.63"},{"v":449.00742990904894,"d":"449.01"},{"v":500.080352352699,"d":"500.08"},{"v":542.6085656417513,"d":"542.61"},{"v":576.6963220510024,"d":"576.70"},{"v":602.6266765758926,"d":"602.63"},{"v":620.7471803876624,"d":"620.75"},{"v":631.3969907951105,"d":"631.40"},{"v":634.8637297522469,"d":"634.86"},{"v":631.360849357404,"d":"631.36"},{"v":621.0192584891399,"d":"621.02"},{"v":603.8897677410387,"d":"603.89"},{"v":579.9553877989295,"d":"579.96"},{"v":549.1547813440195,"d":"549.15"},{"v":511.4203625795653,"d":"511.42"},{"v":466.73667116185055,"d":"466.74"},{"v":415.2263806644581,"d":"415.23"},{"v":357.27159159343057,"d":"357.27"},{"v":293.6746151822486,"d":"293.67"},{"v":225.8512062500224,"d":"225.85"},{"v":156.024615062184,"d":"156.02"},{"v":87.3472119532478,"d":"87.35"},{"v":-2.248392272004174,"d":"-2.25"},{"v":-25.108728728819617,"d":"-25.11"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":155.47594560104181,"d":"155.48"},{"v":212.50816939403848,"d":"212.51"},{"v":268.7536668651518,"d":"268.75"},{"v":321.4400957443796,"d":"321.44"},{"v":368.78111328829806,"d":"368.78"},{"v":409.782102910828,"d":"409.78"},{"v":444.00981360074695,"d":"444.01"},{"v":471.3886407192525,"d":"471.39"},{"v":492.0444742501436,"d":"492.04"},{"v":506.1954011228262,"d":"506.20"},{"v":514.0804400850561,"d":"514.08"},{"v":515.916381372438,"d":"515.92"},{"v":511.8745575241239,"d":"511.87"},{"v":502.07191010933104,"d":"502.07"},{"v":486.5732170309844,"d":"486.57"},{"v":465.40360853409317,"d":"465.40"},{"v":438.5725790182705,"d":"438.57"},{"v":406.1126812478153,"d":"406.11"},{"v":368.1379191208463,"d":"368.14"},{"v":324.92813122258707,"d":"324.93"},{"v":277.0452749726797,"d":"277.05"},{"v":225.4831760241785,"d":"225.48"},{"v":171.840069589995,"d":"171.84"},{"v":118.47810193484295,"d":"118.48"},{"v":68.59338016153426,"d":"68.59"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-25.108728728819617,"d":"-25.11"},{"v":-2.248392272004174,"d":"-2.25"},{"v":174.22977739275535,"d":"174.23"},{"v":250.05468252137956,"d":"250.05"},{"v":322.76480352517916,"d":"322.76"},{"v":389.63153490244974,"d":"389.63"},{"v":449.00742990904894,"d":"449.01"},{"v":500.080352352699,"d":"500.08"},{"v":542.6085656417513,"d":"542.61"},{"v":576.6963220510024,"d":"576.70"},{"v":602.6266765758926,"d":"602.63"},{"v":620.7471803876624,"d":"620.75"},{"v":631.3969907951105,"d":"631.40"},{"v":634.8637297522469,"d":"634.86"},{"v":631.360849357404,"d":"631.36"},{"v":621.0192584891399,"d":"621.02"},{"v":603.8897677410387,"d":"603.89"},{"v":579.9553877989295,"d":"579.96"},{"v":549.1547813440195,"d":"549.15"},{"v":511.4203625795653,"d":"511.42"},{"v":466.73667116185055,"d":"466.74"},{"v":415.2263806644581,"d":"415.23"},{"v":357.27159159343057,"d":"357.27"},{"v":293.6746151822486,"d":"293.67"},{"v":225.8512062500224,"d":"225.85"},{"v":156.024615062184,"d":"156.02"},{"v":87.3472119532478,"d":"87.35"},{"v":-2.248392272004174,"d":"-2.25"},{"v":-25.108728728819617,"d":"-25.11"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":9045.490851445482,"d":"9,045"},"W/m2"]
[null,"Total Directa disponible",{"v":9045.490851445482,"d":"9,045"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":11138.92650298307,"d":"11,139"}]
[null,"Total global ",{"v":11138.92650298307,"d":"11,139"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.1879387256013363,"d":"0.188"},{"v":0.3496090690974937,"d":"0.350"}]
[]
[null,"DICIEMBRE"]
[null,"Declinacion dia tipo",{"v":-23.354300459651345,"d":"-23.35"},{"v":-0.4076094375209411,"d":"-0.41"}]
[null,"ocaso",{"v":-68.43948010016629,"d":"-68.44"},{"v":-1.2346745323016743,"d":"-1.23"}]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"a",{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.610854020563264,"d":"0.611"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.565044554615562,"d":"0.565"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"},{"v":0.9955946996300231,"d":"0.996"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9611513465552403,"d":"0.961"},{"v":0.9321598377044339,"d":"0.932"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8092053855908183,"d":"0.809"},{"v":0.7603825167152518,"d":"0.760"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.6108540205632642,"d":"0.611"},{"v":0.565044554615562,"d":"0.565"},{"v":0.5236403890378366,"d":"0.524"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.45890805959884234,"d":"0.459"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.42005940615408255,"d":"0.420"},{"v":0.4244647065240595,"d":"0.424"},{"v":0.4375467548114382,"d":"0.438"},{"v":0.4589080595988424,"d":"0.459"},{"v":0.48789956844964866,"d":"0.488"},{"v":0.5236403890378365,"d":"0.524"},{"v":0.5650445546155618,"d":"0.565"},{"v":0.610854020563264,"d":"0.611"},{"v":0.6596768894388307,"d":"0.660"},{"v":0.7100297030770413,"d":"0.710"},{"v":0.7603825167152516,"d":"0.760"},{"v":0.8092053855908181,"d":"0.809"},{"v":0.8550148515385207,"d":"0.855"},{"v":0.8964190171162459,"d":"0.896"},{"v":0.9321598377044338,"d":"0.932"},{"v":0.96115134655524,"d":"0.961"},{"v":0.9825126513426443,"d":"0.983"},{"v":0.9955946996300231,"d":"0.996"},{"v":1,"d":"1.000"}]
[null,"b",{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"},{"v":0.5138498817151251,"d":"0.514"}]
[null,"c",{"v":-0.42279514187513445,"d":"-0.423"},{"v":-0.41838984150515757,"d":"-0.418"},{"v":-0.40530779321777877,"d":"-0.405"},{"v":-0.3839464884303745,"d":"-0.384"},{"v":-0.35495497957956823,"d":"-0.355"},{"v":-0.3192141589913804,"d":"-0.319"},{"v":-0.27780999341365514,"d":"-0.278"},{"v":-0.23200052746595257,"d":"-0.232"},{"v":-0.18317765859038604,"d":"-0.183"},{"v":-0.13282484495217567,"d":"-0.133"},{"v":-0.08247203131396524,"d":"-0.082"},{"v":-0.033649162438398494,"d":"-0.034"},{"v":0.012160303509303777,"d":"0.012"},{"v":0.05356446908702904,"d":"0.054"},{"v":0.0893052896752169,"d":"0.089"},{"v":0.11829679852602315,"d":"0.118"},{"v":0.1396581033134274,"d":"0.140"},{"v":0.15274015160080603,"d":"0.153"},{"v":0.157145451970783,"d":"0.157"},{"v":0.15274015160080606,"d":"0.153"},{"v":0.13965810331342737,"d":"0.140"},{"v":0.11829679852602318,"d":"0.118"},{"v":0.08930528967521686,"d":"0.089"},{"v":0.053564469087028985,"d":"0.054"},{"v":0.012160303509303583,"d":"0.012"},{"v":-0.033649162438398716,"d":"-0.034"},{"v":-0.08247203131396524,"d":"-0.082"},{"v":-0.13282484495217578,"d":"-0.133"},{"v":-0.1831776585903862,"d":"-0.183"},{"v":-0.2320005274659528,"d":"-0.232"},{"v":-0.27780999341365514,"d":"-0.278"},{"v":-0.3192141589913804,"d":"-0.319"},{"v":-0.35495497957956834,"d":"-0.355"},{"v":-0.3839464884303747,"d":"-0.384"},{"v":-0.40530779321777877,"d":"-0.405"},{"v":-0.41838984150515757,"d":"-0.418"},{"v":-0.42279514187513445,"d":"-0.423"},{"v":-0.41838984150515757,"d":"-0.418"},{"v":-0.40530779321777877,"d":"-0.405"},{"v":-0.3839464884303747,"d":"-0.384"},{"v":-0.35495497957956834,"d":"-0.355"},{"v":-0.3192141589913804,"d":"-0.319"},{"v":-0.27780999341365514,"d":"-0.278"},{"v":-0.2320005274659528,"d":"-0.232"},{"v":-0.1831776585903862,"d":"-0.183"},{"v":-0.13282484495217578,"d":"-0.133"},{"v":-0.08247203131396524,"d":"-0.082"},{"v":-0.033649162438398716,"d":"-0.034"},{"v":0.012160303509303583,"d":"0.012"},{"v":0.053564469087028985,"d":"0.054"},{"v":0.08930528967521686,"d":"0.089"},{"v":0.11829679852602318,"d":"0.118"},{"v":0.13965810331342737,"d":"0.140"},{"v":0.15274015160080606,"d":"0.153"},{"v":0.157145451970783,"d":"0.157"},{"v":0.15274015160080603,"d":"0.153"},{"v":0.1396581033134274,"d":"0.140"},{"v":0.11829679852602315,"d":"0.118"},{"v":0.0893052896752169,"d":"0.089"},{"v":0.05356446908702904,"d":"0.054"},{"v":0.012160303509303777,"d":"0.012"},{"v":-0.033649162438398494,"d":"-0.034"},{"v":-0.08247203131396524,"d":"-0.082"},{"v":-0.13282484495217567,"d":"-0.133"},{"v":-0.18317765859038604,"d":"-0.183"},{"v":-0.23200052746595257,"d":"-0.232"},{"v":-0.27780999341365514,"d":"-0.278"},{"v":-0.3192141589913804,"d":"-0.319"},{"v":-0.35495497957956823,"d":"-0.355"},{"v":-0.3839464884303745,"d":"-0.384"},{"v":-0.40530779321777877,"d":"-0.405"},{"v":-0.41838984150515757,"d":"-0.418"},{"v":-0.42279514187513445,"d":"-0.423"}]
[null,"alt solar",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-6.809442337969932,"d":"-6.81"},{"v":-1.3932970165682221,"d":"-1.39"},{"v":3.500270315309977,"d":"3.50"},{"v":7.8487217120029955,"d":"7.85"},{"v":11.657964800758908,"d":"11.66"},{"v":14.950786629885378,"d":"14.95"},{"v":17.758162864398777,"d":"17.76"},{"v":20.11337735730501,"d":"20.11"},{"v":22.04835617535155,"d":"22.05"},{"v":23.591550411161816,"d":"23.59"},{"v":24.76681519361029,"d":"24.77"},{"v":25.592883447938796,"d":"25.59"},{"v":26.083164876020536,"d":"26.08"},{"v":26.24569954034866,"d":"26.25"},{"v":26.083164876020536,"d":"26.08"},{"v":25.592883447938796,"d":"25.59"},{"v":24.76681519361029,"d":"24.77"},{"v":23.591550411161816,"d":"23.59"},{"v":22.04835617535155,"d":"22.05"},{"v":20.11337735730501,"d":"20.11"},{"v":17.758162864398777,"d":"17.76"},{"v":14.950786629885378,"d":"14.95"},{"v":11.657964800758908,"d":"11.66"},{"v":7.8487217120029955,"d":"7.85"},{"v":3.500270315309977,"d":"3.50"},{"v":-1.3932970165682221,"d":"-1.39"},{"v":-6.809442337969932,"d":"-6.81"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,"obst. Inf.",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"obst. Sup",1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1]
[null,"obst. TOTAL",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[]
[null,"Latitud",{"v":40.4,"d":"40.40"},null,{"v":0.7051130178057091,"d":"0.71"}]
[null,"Azimut",{"v":15,"d":"15.00"},null,{"v":0.2617993877991494,"d":"0.26"}]
[null,"Inclinacion",{"v":40,"d":"40.00"},null,{"v":0.6981317007977318,"d":"0.70"}]
[null,"Coeficiente refexion",{"v":0,"d":"0.00"}]
[null,"Constante solar extraterrestre (Bo)",{"v":1367,"d":"1,367"},"W/m2"]
[null,"Dia del año",349.5]
[null,"Declinacion . radianes",{"v":-0.4076094375209411,"d":"-0.408"}]
[null,"Ángulo puesta de sol. Radianes. Ws",{"v":1.1944942661010405,"d":"1.194"}]
[null,"Distancia sol - tierra. Bo",{"v":1.0328182359622153,"d":"1.033"},"expresion Duffi y Beckman"]
[null,"Factor angulo solar",{"v":0.34333162390383465,"d":"0.343"}]
[null,"Ho. Irradiacion Extraterreste sobre sup. Horizontal",{"v":3703.1183207463055,"d":"3,703"}]
[null,"H1",{"v":38791.93911776661,"d":"38,792"}]
[null,"H2",{"v":0.650226992576542,"d":"0.650"}]
[null,"H3",{"v":-0.3068953686727074,"d":"-0.307"}]
[null,"H horizontal diaria (W/m2 dia) s/ localidad",{"v":1872.701111111111,"d":"1,873"},"W/m2 dia"]
[null,"Indice de claridad Kt",{"v":0.5057092290623049,"d":"0.506"}]
[null,"Fraccion difusa diaria promedio",{"v":0.35769976292846456,"d":"0.358"},"Correlacion Collares-Pereira "]
[null,"Factor A Lui y Jordan",{"v":0.4826171532469664,"d":"0.483"},"parametros 5 estaciones EEUU"]
[null,"Factor B Lui y Jordan",{"v":0.5909372867766569,"d":"0.591"},"parametros 5 estaciones EEUU"]
[]
[null,"AZIMUT",-180,-175,-170,-165,-160,-155,-150,-145,-140,-135,-130,-125,-120,-115,-110,-105,-100,-95,-90,-85,-80,-75,-70,-65,-60,-55,-50,-45,-40,-35,-30,-25,-20,-15,-10,-5,0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90,95,100,105,110,115,120,125,130,135,140,145,150,155,160,165,170,175,180]
[null,"Az radianes",{"v":-3.141592653589793,"d":"-3.14"},{"v":-3.0543261909900763,"d":"-3.05"},{"v":-2.9670597283903604,"d":"-2.97"},{"v":-2.8797932657906435,"d":"-2.88"},{"v":-2.792526803190927,"d":"-2.79"},{"v":-2.705260340591211,"d":"-2.71"},{"v":-2.6179938779914944,"d":"-2.62"},{"v":-2.5307274153917776,"d":"-2.53"},{"v":-2.443460952792061,"d":"-2.44"},{"v":-2.356194490192345,"d":"-2.36"},{"v":-2.2689280275926285,"d":"-2.27"},{"v":-2.1816615649929116,"d":"-2.18"},{"v":-2.0943951023931953,"d":"-2.09"},{"v":-2.007128639793479,"d":"-2.01"},{"v":-1.9198621771937625,"d":"-1.92"},{"v":-1.8325957145940461,"d":"-1.83"},{"v":-1.7453292519943295,"d":"-1.75"},{"v":-1.6580627893946132,"d":"-1.66"},{"v":-1.5707963267948966,"d":"-1.57"},{"v":-1.4835298641951802,"d":"-1.48"},{"v":-1.3962634015954636,"d":"-1.40"},{"v":-1.3089969389957472,"d":"-1.31"},{"v":-1.2217304763960306,"d":"-1.22"},{"v":-1.1344640137963142,"d":"-1.13"},{"v":-1.0471975511965976,"d":"-1.05"},{"v":-0.9599310885968813,"d":"-0.96"},{"v":-0.8726646259971648,"d":"-0.87"},{"v":-0.7853981633974483,"d":"-0.79"},{"v":-0.6981317007977318,"d":"-0.70"},{"v":-0.6108652381980153,"d":"-0.61"},{"v":-0.5235987755982988,"d":"-0.52"},{"v":-0.4363323129985824,"d":"-0.44"},{"v":-0.3490658503988659,"d":"-0.35"},{"v":-0.2617993877991494,"d":"-0.26"},{"v":-0.17453292519943295,"d":"-0.17"},{"v":-0.08726646259971647,"d":"-0.09"},{"v":0,"d":"0.00"},{"v":0.08726646259971647,"d":"0.09"},{"v":0.17453292519943295,"d":"0.17"},{"v":0.2617993877991494,"d":"0.26"},{"v":0.3490658503988659,"d":"0.35"},{"v":0.4363323129985824,"d":"0.44"},{"v":0.5235987755982988,"d":"0.52"},{"v":0.6108652381980153,"d":"0.61"},{"v":0.6981317007977318,"d":"0.70"},{"v":0.7853981633974483,"d":"0.79"},{"v":0.8726646259971648,"d":"0.87"},{"v":0.9599310885968813,"d":"0.96"},{"v":1.0471975511965976,"d":"1.05"},{"v":1.1344640137963142,"d":"1.13"},{"v":1.2217304763960306,"d":"1.22"},{"v":1.3089969389957472,"d":"1.31"},{"v":1.3962634015954636,"d":"1.40"},{"v":1.4835298641951802,"d":"1.48"},{"v":1.5707963267948966,"d":"1.57"},{"v":1.6580627893946132,"d":"1.66"},{"v":1.7453292519943295,"d":"1.75"},{"v":1.8325957145940461,"d":"1.83"},{"v":1.9198621771937625,"d":"1.92"},{"v":2.007128639793479,"d":"2.01"},{"v":2.0943951023931953,"d":"2.09"},{"v":2.1816615649929116,"d":"2.18"},{"v":2.2689280275926285,"d":"2.27"},{"v":2.356194490192345,"d":"2.36"},{"v":2.443460952792061,"d":"2.44"},{"v":2.5307274153917776,"d":"2.53"},{"v":2.6179938779914944,"d":"2.62"},{"v":2.705260340591211,"d":"2.71"},{"v":2.792526803190927,"d":"2.79"},{"v":2.8797932657906435,"d":"2.88"},{"v":2.9670597283903604,"d":"2.97"},{"v":3.0543261909900763,"d":"3.05"},{"v":3.141592653589793,"d":"3.14"}]
[null,"alt solar (grados)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":-6.809442337969932,"d":"-6.81"},{"v":-1.3932970165682221,"d":"-1.39"},{"v":3.500270315309977,"d":"3.50"},{"v":7.8487217120029955,"d":"7.85"},{"v":11.657964800758908,"d":"11.66"},{"v":14.950786629885378,"d":"14.95"},{"v":17.758162864398777,"d":"17.76"},{"v":20.11337735730501,"d":"20.11"},{"v":22.04835617535155,"d":"22.05"},{"v":23.591550411161816,"d":"23.59"},{"v":24.76681519361029,"d":"24.77"},{"v":25.592883447938796,"d":"25.59"},{"v":26.083164876020536,"d":"26.08"},{"v":26.24569954034866,"d":"26.25"},{"v":26.083164876020536,"d":"26.08"},{"v":25.592883447938796,"d":"25.59"},{"v":24.76681519361029,"d":"24.77"},{"v":23.591550411161816,"d":"23.59"},{"v":22.04835617535155,"d":"22.05"},{"v":20.11337735730501,"d":"20.11"},{"v":17.758162864398777,"d":"17.76"},{"v":14.950786629885378,"d":"14.95"},{"v":11.657964800758908,"d":"11.66"},{"v":7.8487217120029955,"d":"7.85"},{"v":3.500270315309977,"d":"3.50"},{"v":-1.3932970165682221,"d":"-1.39"},{"v":-6.809442337969932,"d":"-6.81"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"ang horario (grados)",{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":68.43948010016629,"d":"68.44"},{"v":78.58612761574815,"d":"78.59"},{"v":70.56693842088724,"d":"70.57"},{"v":62.947340204169315,"d":"62.95"},{"v":55.75000390502464,"d":"55.75"},{"v":48.96605578191773,"d":"48.97"},{"v":42.56673594370141,"d":"42.57"},{"v":36.51221008239814,"d":"36.51"},{"v":30.757522685342188,"d":"30.76"},{"v":25.25625460767566,"d":"25.26"},{"v":19.962539710208517,"d":"19.96"},{"v":14.831991606958345,"d":"14.83"},{"v":9.821943753672468,"d":"9.82"},{"v":4.8912755257772575,"d":"4.89"},{"v":0,"d":"0.00"},{"v":-4.8912755257772575,"d":"-4.89"},{"v":-9.821943753672468,"d":"-9.82"},{"v":-14.831991606958345,"d":"-14.83"},{"v":-19.962539710208517,"d":"-19.96"},{"v":-25.25625460767566,"d":"-25.26"},{"v":-30.757522685342188,"d":"-30.76"},{"v":-36.51221008239814,"d":"-36.51"},{"v":-42.56673594370141,"d":"-42.57"},{"v":-48.96605578191773,"d":"-48.97"},{"v":-55.75000390502464,"d":"-55.75"},{"v":-62.947340204169315,"d":"-62.95"},{"v":-70.56693842088724,"d":"-70.57"},{"v":-78.58612761574815,"d":"-78.59"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"},{"v":-68.43948010016629,"d":"-68.44"}]
[null,"Factor inclinación",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.694102641325218,"d":"2.69"},{"v":17.921223219432125,"d":"17.92"},{"v":-8.816153376669002,"d":"-8.82"},{"v":-4.5857265742781,"d":"-4.59"},{"v":-3.46407075999429,"d":"-3.46"},{"v":-2.9476945732687274,"d":"-2.95"},{"v":-2.6520855720700416,"d":"-2.65"},{"v":-2.4614662031479604,"d":"-2.46"},{"v":-2.329030229290424,"d":"-2.33"},{"v":-2.2323178533991443,"d":"-2.23"},{"v":-2.159282961595738,"d":"-2.16"},{"v":-2.1029665993722224,"d":"-2.10"},{"v":-2.0591651497543424,"d":"-2.06"},{"v":-2.0253132488479646,"d":"-2.03"},{"v":-1.9999258601711931,"d":"-2.00"},{"v":-1.9823357596609523,"d":"-1.98"},{"v":-1.9726243936508474,"d":"-1.97"},{"v":-1.9717333148007399,"d":"-1.97"},{"v":-1.9818315574145142,"d":"-1.98"},{"v":-2.007179311718042,"d":"-2.01"},{"v":-2.0561725576028755,"d":"-2.06"},{"v":-2.1467487964464493,"d":"-2.15"},{"v":-2.323750663447634,"d":"-2.32"},{"v":-2.7367010921829884,"d":"-2.74"},{"v":-4.360221564265979,"d":"-4.36"},{"v":6.073970248694181,"d":"6.07"},{"v":0.16870947344497925,"d":"0.17"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Correccion valores negativos",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.694102641325218,"d":"2.69"},{"v":17.921223219432125,"d":"17.92"},{"v":8.816153376669002,"d":"8.82"},{"v":4.5857265742781,"d":"4.59"},{"v":3.46407075999429,"d":"3.46"},{"v":2.9476945732687274,"d":"2.95"},{"v":2.6520855720700416,"d":"2.65"},{"v":2.4614662031479604,"d":"2.46"},{"v":2.329030229290424,"d":"2.33"},{"v":2.2323178533991443,"d":"2.23"},{"v":2.159282961595738,"d":"2.16"},{"v":2.1029665993722224,"d":"2.10"},{"v":2.0591651497543424,"d":"2.06"},{"v":2.0253132488479646,"d":"2.03"},{"v":1.9999258601711931,"d":"2.00"},{"v":1.9823357596609523,"d":"1.98"},{"v":1.9726243936508474,"d":"1.97"},{"v":1.9717333148007399,"d":"1.97"},{"v":1.9818315574145142,"d":"1.98"},{"v":2.007179311718042,"d":"2.01"},{"v":2.0561725576028755,"d":"2.06"},{"v":2.1467487964464493,"d":"2.15"},{"v":2.323750663447634,"d":"2.32"},{"v":2.7367010921829884,"d":"2.74"},{"v":4.360221564265979,"d":"4.36"},{"v":6.073970248694181,"d":"6.07"},{"v":0.16870947344497925,"d":"0.17"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiacion H GLOBAL (distribucion Lui y Jordan)",{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":-50.75658075878137,"d":"-50.76"},{"v":-11.791941603329413,"d":"-11.79"},{"v":32.753838897750676,"d":"32.75"},{"v":79.4830263979849,"d":"79.48"},{"v":125.60208275099195,"d":"125.60"},{"v":169.0675611187766,"d":"169.07"},{"v":208.5279117942248,"d":"208.53"},{"v":243.17777355609832,"d":"243.18"},{"v":272.5987779814395,"d":"272.60"},{"v":296.62184280013105,"d":"296.62"},{"v":315.2214360349813,"d":"315.22"},{"v":328.440378262662,"d":"328.44"},{"v":336.3395722654834,"d":"336.34"},{"v":338.96674408290386,"d":"338.97"},{"v":336.3395722654834,"d":"336.34"},{"v":328.440378262662,"d":"328.44"},{"v":315.2214360349813,"d":"315.22"},{"v":296.62184280013105,"d":"296.62"},{"v":272.5987779814395,"d":"272.60"},{"v":243.17777355609832,"d":"243.18"},{"v":208.5279117942248,"d":"208.53"},{"v":169.0675611187766,"d":"169.07"},{"v":125.60208275099195,"d":"125.60"},{"v":79.4830263979849,"d":"79.48"},{"v":32.753838897750676,"d":"32.75"},{"v":-11.791941603329413,"d":"-11.79"},{"v":-50.75658075878137,"d":"-50.76"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"},{"v":5.817314386794632e-14,"d":"0.00"}]
[null,"Radiacion H DIFUSA (distribucion Lui y Jordan)",{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":-30.281542912730714,"d":"-30.28"},{"v":-6.209980187791299,"d":"-6.21"},{"v":15.592678391082593,"d":"15.59"},{"v":34.87619706837343,"d":"34.88"},{"v":51.6073161159618,"d":"51.61"},{"v":65.88910486294995,"d":"65.89"},{"v":77.89539043644137,"d":"77.90"},{"v":87.82487253202947,"d":"87.82"},{"v":95.8723697629989,"d":"95.87"},{"v":102.21252110304691,"d":"102.21"},{"v":106.99155745318797,"d":"106.99"},{"v":110.32381760775252,"d":"110.32"},{"v":112.29075386476673,"d":"112.29"},{"v":112.94101116699788,"d":"112.94"},{"v":112.29075386476673,"d":"112.29"},{"v":110.32381760775252,"d":"110.32"},{"v":106.99155745318797,"d":"106.99"},{"v":102.21252110304691,"d":"102.21"},{"v":95.8723697629989,"d":"95.87"},{"v":87.82487253202947,"d":"87.82"},{"v":77.89539043644137,"d":"77.90"},{"v":65.88910486294995,"d":"65.89"},{"v":51.6073161159618,"d":"51.61"},{"v":34.87619706837343,"d":"34.88"},{"v":15.592678391082593,"d":"15.59"},{"v":-6.209980187791299,"d":"-6.21"},{"v":-30.281542912730714,"d":"-30.28"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"},{"v":2.9735928541106045e-14,"d":"0.00"}]
[null,"Total Directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":151.29542314842053,"d":"151.30"},{"v":204.55472265108708,"d":"204.55"},{"v":256.32310749300905,"d":"256.32"},{"v":304.13857558354505,"d":"304.14"},{"v":346.44862513610894,"d":"346.45"},{"v":382.3959154317356,"d":"382.40"},{"v":411.6011470546678,"d":"411.60"},{"v":433.9833996916185,"d":"433.98"},{"v":449.6272289168156,"d":"449.63"},{"v":458.6918418272201,"d":"458.69"},{"v":461.3535186943953,"d":"461.35"},{"v":457.77291145515585,"d":"457.77"},{"v":448.0810258603928,"d":"448.08"},{"v":432.38025796048424,"d":"432.38"},{"v":410.7593379773997,"d":"410.76"},{"v":383.3233362979551,"d":"383.32"},{"v":350.2419728358254,"d":"350.24"},{"v":311.8211289508916,"d":"311.82"},{"v":268.6030055463458,"d":"268.60"},{"v":221.4982267863985,"d":"221.50"},{"v":171.94538805980417,"d":"171.95"},{"v":122.07555854516788,"d":"122.08"},{"v":74.82646210900384,"d":"74.83"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Difusa (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":-26.739275295048472,"d":"-26.74"},{"v":-5.483550501263885,"d":"-5.48"},{"v":13.76868151295639,"d":"13.77"},{"v":30.79645701486164,"d":"30.80"},{"v":45.57040692543941,"d":"45.57"},{"v":58.18154375264819,"d":"58.18"},{"v":68.78336071243024,"d":"68.78"},{"v":77.55131405141161,"d":"77.55"},{"v":84.65743293429607,"d":"84.66"},{"v":90.25592745560863,"d":"90.26"},{"v":94.47592275042373,"d":"94.48"},{"v":97.41838251492149,"d":"97.42"},{"v":99.15523093825608,"d":"99.16"},{"v":99.72942258585752,"d":"99.73"},{"v":99.15523093825608,"d":"99.16"},{"v":97.41838251492149,"d":"97.42"},{"v":94.47592275042373,"d":"94.48"},{"v":90.25592745560863,"d":"90.26"},{"v":84.65743293429607,"d":"84.66"},{"v":77.55131405141161,"d":"77.55"},{"v":68.78336071243024,"d":"68.78"},{"v":58.18154375264819,"d":"58.18"},{"v":45.57040692543941,"d":"45.57"},{"v":30.79645701486164,"d":"30.80"},{"v":13.76868151295639,"d":"13.77"},{"v":-5.483550501263885,"d":"-5.48"},{"v":-26.739275295048472,"d":"-26.74"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Reflejada (plano incl)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"TOTAL (W/m2)",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":-26.739275295048472,"d":"-26.74"},{"v":-5.483550501263885,"d":"-5.48"},{"v":165.06410466137692,"d":"165.06"},{"v":235.3511796659487,"d":"235.35"},{"v":301.89351441844843,"d":"301.89"},{"v":362.3201193361932,"d":"362.32"},{"v":415.2319858485392,"d":"415.23"},{"v":459.9472294831472,"d":"459.95"},{"v":496.2585799889639,"d":"496.26"},{"v":524.2393271472272,"d":"524.24"},{"v":544.1031516672393,"d":"544.10"},{"v":556.1102243421416,"d":"556.11"},{"v":560.5087496326514,"d":"560.51"},{"v":557.5023340410133,"d":"557.50"},{"v":547.2362567986489,"d":"547.24"},{"v":529.7986404754057,"d":"529.80"},{"v":505.2352607278234,"d":"505.24"},{"v":473.57926375356374,"d":"473.58"},{"v":434.89940577012146,"d":"434.90"},{"v":389.3724430023032,"d":"389.37"},{"v":337.38636625877604,"d":"337.39"},{"v":279.6797705390467,"d":"279.68"},{"v":217.5157949852436,"d":"217.52"},{"v":152.87201556002952,"d":"152.87"},{"v":88.59514362196023,"d":"88.60"},{"v":-5.483550501263885,"d":"-5.48"},{"v":-26.739275295048472,"d":"-26.74"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Directa recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":151.29542314842053,"d":"151.30"},{"v":204.55472265108708,"d":"204.55"},{"v":256.32310749300905,"d":"256.32"},{"v":304.13857558354505,"d":"304.14"},{"v":346.44862513610894,"d":"346.45"},{"v":382.3959154317356,"d":"382.40"},{"v":411.6011470546678,"d":"411.60"},{"v":433.9833996916185,"d":"433.98"},{"v":449.6272289168156,"d":"449.63"},{"v":458.6918418272201,"d":"458.69"},{"v":461.3535186943953,"d":"461.35"},{"v":457.77291145515585,"d":"457.77"},{"v":448.0810258603928,"d":"448.08"},{"v":432.38025796048424,"d":"432.38"},{"v":410.7593379773997,"d":"410.76"},{"v":383.3233362979551,"d":"383.32"},{"v":350.2419728358254,"d":"350.24"},{"v":311.8211289508916,"d":"311.82"},{"v":268.6030055463458,"d":"268.60"},{"v":221.4982267863985,"d":"221.50"},{"v":171.94538805980417,"d":"171.95"},{"v":122.07555854516788,"d":"122.08"},{"v":74.82646210900384,"d":"74.83"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Radiación Global recibida",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":-26.739275295048472,"d":"-26.74"},{"v":-5.483550501263885,"d":"-5.48"},{"v":165.06410466137692,"d":"165.06"},{"v":235.3511796659487,"d":"235.35"},{"v":301.89351441844843,"d":"301.89"},{"v":362.3201193361932,"d":"362.32"},{"v":415.2319858485392,"d":"415.23"},{"v":459.9472294831472,"d":"459.95"},{"v":496.2585799889639,"d":"496.26"},{"v":524.2393271472272,"d":"524.24"},{"v":544.1031516672393,"d":"544.10"},{"v":556.1102243421416,"d":"556.11"},{"v":560.5087496326514,"d":"560.51"},{"v":557.5023340410133,"d":"557.50"},{"v":547.2362567986489,"d":"547.24"},{"v":529.7986404754057,"d":"529.80"},{"v":505.2352607278234,"d":"505.24"},{"v":473.57926375356374,"d":"473.58"},{"v":434.89940577012146,"d":"434.90"},{"v":389.3724430023032,"d":"389.37"},{"v":337.38636625877604,"d":"337.39"},{"v":279.6797705390467,"d":"279.68"},{"v":217.5157949852436,"d":"217.52"},{"v":152.87201556002952,"d":"152.87"},{"v":88.59514362196023,"d":"88.60"},{"v":-5.483550501263885,"d":"-5.48"},{"v":-26.739275295048472,"d":"-26.74"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":2.6257485680501673e-14,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total Directa recibida",{"v":7513.74211801345,"d":"7,514"},"W/m2"]
[null,"Total Directa disponible",{"v":7513.74211801345,"d":"7,514"},"W/m2"]
[null,"Obstruccion directa",{"v":0,"d":"0.000%"}]
[null,"Total global recibida",{"v":9070.25521013319,"d":"9,070"}]
[null,"Total global ",{"v":9070.25521013319,"d":"9,070"},"W/m2","% difusa","Fd"]
[null,"Obstrucción global",{"v":0,"d":"0.000%"},null,{"v":0.17160631713877472,"d":"0.172"},{"v":0.35769976292846456,"d":"0.358"}]
[]
[null,"FACTORES SOLARES ANUALES"]
[]
[null,"Mes","Ene","Feb","Mar","Abr","May","Jun","Jul","Ago","Sep","Oct","Nov","Dic"]
[null,"Radiacion horizontal (W/m2 dia)",{"v":2273.278888888889,"d":"2,273.28"},{"v":3254.6944444444443,"d":"3,254.69"},{"v":4656.716666666666,"d":"4,656.72"},{"v":5758.305555555556,"d":"5,758.31"},{"v":6609.533333333333,"d":"6,609.53"},{"v":7751.179999999999,"d":"7,751.18"},{"v":8051.613333333331,"d":"8,051.61"},{"v":7010.111111111111,"d":"7,010.11"},{"v":5477.901111111111,"d":"5,477.90"},{"v":3565.1422222222222,"d":"3,565.14"},{"v":2433.51,"d":"2,433.51"},{"v":1872.701111111111,"d":"1,872.70"}]
[null,"Total Directa recibida",{"v":9045.043020116778,"d":"9,045.04"},{"v":11321.59345145366,"d":"11,321.59"},{"v":13905.372119038626,"d":"13,905.37"},{"v":14230.866388136234,"d":"14,230.87"},{"v":14364.091929026283,"d":"14,364.09"},{"v":16926.27494409376,"d":"16,926.27"},{"v":18619.752527990036,"d":"18,619.75"},{"v":17611.360125721432,"d":"17,611.36"},{"v":15606.961006815707,"d":"15,606.96"},{"v":11427.49280541107,"d":"11,427.49"},{"v":9045.490851445482,"d":"9,045.49"},{"v":7513.74211801345,"d":"7,513.74"}]
[null,"Total Directa disponible",{"v":9045.043020116778,"d":"9,045.04"},{"v":11321.59345145366,"d":"11,321.59"},{"v":13905.372119038626,"d":"13,905.37"},{"v":14230.866388136234,"d":"14,230.87"},{"v":14364.091929026283,"d":"14,364.09"},{"v":16926.27494409376,"d":"16,926.27"},{"v":18619.752527990036,"d":"18,619.75"},{"v":17611.360125721432,"d":"17,611.36"},{"v":15606.961006815707,"d":"15,606.96"},{"v":11427.49280541107,"d":"11,427.49"},{"v":9045.490851445482,"d":"9,045.49"},{"v":7513.74211801345,"d":"7,513.74"}]
[null,"Obstruccion directa",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[null,"Total global recibida",{"v":10987.31219431356,"d":"10,987.31"},{"v":14236.77115342664,"d":"14,236.77"},{"v":18642.557714944214,"d":"18,642.56"},{"v":21191.032810473782,"d":"21,191.03"},{"v":23201.61817919323,"d":"23,201.62"},{"v":26610.450659245682,"d":"26,610.45"},{"v":27951.131191938843,"d":"27,951.13"},{"v":25407.478876547415,"d":"25,407.48"},{"v":21253.955191838173,"d":"21,253.96"},{"v":14948.67234173916,"d":"14,948.67"},{"v":11138.92650298307,"d":"11,138.93"},{"v":9070.25521013319,"d":"9,070.26"}]
[null,"Total global ",{"v":10987.31219431356,"d":"10,987.31"},{"v":14236.77115342664,"d":"14,236.77"},{"v":18642.557714944214,"d":"18,642.56"},{"v":21191.032810473782,"d":"21,191.03"},{"v":23201.61817919323,"d":"23,201.62"},{"v":26610.450659245682,"d":"26,610.45"},{"v":27951.131191938843,"d":"27,951.13"},{"v":25407.478876547415,"d":"25,407.48"},{"v":21253.955191838173,"d":"21,253.96"},{"v":14948.67234173916,"d":"14,948.67"},{"v":11138.92650298307,"d":"11,138.93"},{"v":9070.25521013319,"d":"9,070.26"}]
[null,"Obstrucción global",{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[]
[null,null,"% obtruc","factor"]
[null,"Directa invierno",{"v":0,"d":"0.000%"},{"v":1,"d":"1.000"}]
[null,"Directa verano",{"v":0,"d":"0.000%"},{"v":1,"d":"1.000"}]
[]
[null,"Global invierno",{"v":0,"d":"0.000%"},{"v":1,"d":"1.000"}]
[null,"Global verano",{"v":0,"d":"0.000%"},{"v":1,"d":"1.000"}]
[]
[null,"Directa anual",{"v":1,"d":"100.000%"},{"v":0,"d":"0.000"}]
[null,"Global anual",{"v":1,"d":"100.000%"},{"v":0,"d":"0.000"}]
[]
[null,"Curva rendimiento"]
[]
[null,"K0",{"v":0.79,"d":"0.790"},null,"Rango",40]
[null,"K1",{"v":2.4141,"d":"2.414"},null,null,70]
[null,"K2",0.049]
[null,null,"STC","Verano","Invierno"]
[null,"Tm-Ta",800,{"v":922.2234164280594,"d":"922"},{"v":560.5087496326514,"d":"561"}]
[null,0,0.79,0.79,0.79]
[null,5,{"v":0.773380625,"d":"0.77"},{"v":0.775583211439701,"d":"0.78"},{"v":0.7662795852719273,"d":"0.77"}]
[null,10,{"v":0.75369875,"d":"0.75"},{"v":0.7585097998134973,"d":"0.76"},{"v":0.7381881415427806,"d":"0.74"}]
[null,15,{"v":0.730954375,"d":"0.73"},{"v":0.7387797651213893,"d":"0.74"},{"v":0.7057256688125599,"d":"0.71"}]
[null,20,{"v":0.7051475,"d":"0.71"},{"v":0.7163931073633769,"d":"0.72"},{"v":0.6688921670812654,"d":"0.67"}]
[null,25,{"v":0.676278125,"d":"0.68"},{"v":0.69134982653946,"d":"0.69"},{"v":0.627687636348897,"d":"0.63"},{"$nulls":8},40,0]
[null,30,{"v":0.64434625,"d":"0.64"},{"v":0.6636499226496385,"d":"0.66"},{"v":0.5821120766154546,"d":"0.58"},{"$nulls":8},40,1]
[null,35,{"v":0.6093518750000001,"d":"0.61"},{"v":0.6332933956939126,"d":"0.63"},{"v":0.5321654878809382,"d":"0.53"}]
[null,40,{"v":0.5712950000000001,"d":"0.57"},{"v":0.6002802456722823,"d":"0.60"},{"v":0.477847870145348,"d":"0.48"},{"$nulls":8},70,0]
[null,45,{"v":0.530175625,"d":"0.53"},{"v":0.5646104725847474,"d":"0.56"},{"v":0.41915922340868395,"d":"0.42"},{"$nulls":8},70,1]
[null,50,{"v":0.48599375000000006,"d":"0.49"},{"v":0.5262840764313081,"d":"0.53"},{"v":0.3560995476709459,"d":"0.36"}]
[null,55,{"v":0.4387493750000001,"d":"0.44"},{"v":0.4853010572119645,"d":"0.49"},{"v":0.28866884293213396,"d":"0.29"}]
[null,60,{"v":0.3884425,"d":"0.39"},{"v":0.4416614149267162,"d":"0.44"},{"v":0.2168671091922481,"d":"0.22"}]
[null,65,{"v":0.335073125,"d":"0.34"},{"v":0.39536514957556357,"d":"0.40"},{"v":0.1406943464512883,"d":"0.14"}]
[null,70,{"v":0.27864125,"d":"0.28"},{"v":0.3464122611585065,"d":"0.35"},{"v":0.060150554709254456,"d":"0.06"}]
[null,75,{"v":0.21914687500000002,"d":"0.22"},{"v":0.2948027496755448,"d":"0.29"},""]
[null,80,{"v":0.15659,"d":"0.16"},{"v":0.2405366151266788,"d":"0.24"},""]
[null,85,{"v":0.09097062499999997,"d":"0.09"},{"v":0.18361385751190828,"d":"0.18"},""]
[null,90,{"v":0.02228874999999997,"d":"0.02"},{"v":0.1240344768312332,"d":"0.12"},""]
[null,95,"",{"v":0.061798473084653804,"d":"0.06"},""]
[null,100,"","",""]

{"sheet":"Localidades","index":20,"n_rows":118,"n_cols":19,"rows_kept":118,"hidden":true,"merged":[[1,6,1,17],[5,6,5,17],[9,6,9,17],[64,6,64,17]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":2}
[]
["DT","Provincia (Pr)","Madrid",{"$nulls":3},"Temperatura Agua s/ CTE HE4 2013"]
["B","Capital (Cp)",40.4,{"$nulls":3},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic.","Altura REF"]
["B","Zona HE1","D3",{"$nulls":3},8,8,10,12,14,17,20,19,17,13,10,8,655]
["B","Zona HE4","IV",{"$nulls":3},6,7,8,9,10,11,12,13,14,15,16,17,18]
[{"$nulls":6},"Temperatura median en horas diurnas"]
[{"$nulls":6},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic."]
[{"$nulls":6},6.2,7.4,9.9,12.2,16,20.7,24.4,23.9,20.5,14.7,9.4,6.4]
[]
[{"$nulls":6},"Temperatura Agua s/ CTE HE4 2013"]
[null,null,"Latitud","Zona Climática","Zona Solar","Altitud capital","Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic.","Altura REF"]
[null,"Albacete",39,"D3","V",686,7,8,9,11,14,17,19,19,17,13,9,7,686]
[null,"Alicante",38.4,"B4","V",7,11,12,13,14,16,18,20,20,19,16,13,12,8]
[null,"Almería",36.9,"A4","V",65,12,12,13,14,16,18,20,21,19,17,14,12,16]
[null,"Ávila",40.7,"E1","IV",1126,6,6,7,9,11,14,17,16,14,11,8,6,1131]
[null,"Badajoz",38.9,"C4","V",186,9,10,11,13,15,18,20,20,18,15,12,9,186]
[null,"Barcelona",41.4,"C2","II",95,9,10,11,12,14,17,19,19,17,15,12,10,12]
[null,"Bilbao",43.3,"C1","I",32,9,10,10,11,13,15,17,17,16,14,11,10,6]
[null,"Burgos",42.3,"E1","II",929,5,6,7,9,11,13,16,16,14,11,7,6,929]
[null,"Cáceres",39.5,"C4","V",459,9,10,11,12,14,18,21,20,19,15,11,9,459]
[null,"Cádiz",36.5,"A3","IV",28,12,12,13,14,16,18,19,20,19,17,14,12,14]
[null,"Castellón",40,"B3","IV",27,10,11,12,13,15,18,19,20,18,16,12,11,27]
[null,"Ceuta",35.9,"B3","V",206,11,11,12,13,14,16,18,18,17,15,13,12,40]
[null,"Ciudad Real",39,"D3","IV",628,7,8,10,11,14,17,20,20,17,13,10,7,628]
[null,"Córdoba",37.9,"B4","IV",128,10,11,12,14,16,19,21,21,19,16,12,10,106]
[null,"Coruña, La",43.4,"C1","I",54,10,10,11,12,13,14,16,16,15,14,12,11,26]
[null,"Cuenca",40.1,"D2","III",949,6,7,8,10,13,16,18,18,16,12,9,7,999]
[null,"Gerona",42,"D2","III",95,8,9,10,11,14,16,19,18,17,14,10,9,70]
[null,"Granada",37.2,"C3","IV",775,8,9,10,12,14,17,20,19,17,14,11,8,683]
[null,"Guadalajara",40.6,"D3","IV",685,7,8,9,11,14,17,19,19,16,13,9,7,685]
[null,"Huelva",37.3,"A4","V",4,12,12,13,14,16,18,20,20,19,17,14,12,30]
[null,"Huesca",42.1,"D2","III",488,7,8,10,11,14,16,19,18,17,13,9,7,488]
[null,"Jaén",37.8,"C4","IV",586,9,10,11,13,16,19,21,21,19,15,12,9,568]
[null,"León",42.6,"E1","III",908,6,6,8,9,12,14,16,16,15,11,8,6,838]
[null,"Lleida",41.7,"D3","III",323,7,9,10,12,15,17,20,19,17,14,10,7,182]
[null,"Logroño",42.5,"D2","II",380,7,8,10,11,13,16,18,18,16,13,10,8,385]
[null,"Lugo",43,"D1","II",465,7,8,9,10,11,13,15,15,14,12,9,8,454]
[null,"Madrid",40.4,"D3","IV",667,8,8,10,12,14,17,20,19,17,13,10,8,655]
[null,"Málaga",36.7,"A3","IV",40,12,12,13,14,16,18,20,20,19,16,14,12,11]
[null,"Melilla",35.3,"A3","V",47,12,13,13,14,16,18,20,20,19,17,14,13,15]
[null,"Murcia",38,"B3","IV",42,11,11,12,13,15,17,19,20,18,16,13,11,39]
[null,"Orense",42.3,"D2","II",139,8,10,11,12,14,16,18,18,17,13,11,9,139]
[null,"Oviedo",43.4,"D1","I",232,9,9,10,10,12,14,15,16,15,13,10,9,232]
[null,"Palencia",42,"D1","II",734,6,7,8,10,12,15,17,17,15,12,9,6,734]
[null,"Palma de Mallorca",39.6,"B3","IV",28,11,11,12,13,15,18,20,20,19,17,14,12,15]
[null,"Pamplona",42.8,"D1","II",449,7,8,9,10,12,15,17,17,16,13,9,7,490]
[null,"Pontevedra",42.4,"C1","I",19,10,11,11,13,14,16,17,17,16,14,12,10,27]
[null,"Salamanca",41,"D2","III",803,6,7,8,10,12,15,17,17,15,12,8,6,800]
[null,"San Sebastian",{"v":43.3,"d":"43.30"},"D1","I",181,9,9,10,11,12,14,16,16,15,14,11,9,12]
[null,"Santander",43.5,"C1","I",69,10,10,11,11,13,15,16,16,16,14,12,10,11]
[null,"Segovia",41,"D2","III",1002,6,7,8,10,12,15,18,18,15,12,8,6,1002]
[null,"Sevilla",37.4,"B4","V",30,11,11,13,14,16,19,21,21,20,16,13,11,11]
[null,"Soria",41.8,"E1","III",1063,5,6,7,9,11,14,17,16,14,11,8,6,1063]
[null,"Tarragona",41.1,"B3","III",60,10,11,12,14,16,18,20,20,19,16,12,11,69]
[null,"Teruel",40.4,"D2","III",915,6,7,8,10,12,15,18,17,15,12,8,6,912]
[null,"Toledo",39.9,"C4","IV",540,8,9,11,12,15,18,21,20,18,14,11,8,629]
[null,"Valencia",39.5,"B3","IV",10,10,11,12,13,15,17,19,20,18,16,13,11,13]
[null,"Valladolid",41.7,"D2","II",694,6,8,9,10,12,15,18,18,16,12,9,7,698]
[null,"Vitoria",42.9,"D1","I",542,7,7,8,10,12,14,16,16,14,12,8,7,540]
[null,"Zamora",41.5,"D2","III",649,6,8,9,10,13,16,18,18,16,12,9,7,649]
[null,"Zaragoza",41.7,"D3","IV",200,8,9,10,12,15,17,20,19,17,14,10,8,199]
[null,"Palmas de Gran Canarias",28.2,"alfa3","V",6,15,15,16,16,17,18,19,19,19,18,17,16,13]
[null,"Santa Cruz de Tenerife",28.5,"alfa3","V",37,15,15,16,16,17,18,20,20,20,18,17,16,5]
[]
[{"$nulls":6},"Temperatura media diurna. Guia IDAE ASIT UNE 94003:2007"]
[{"$nulls":6},"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Sept.","Oct.","Nov.","Dic."]
[null,"Albacete",{"$nulls":4},{"v":5,"d":"5.00"},{"v":6.3,"d":"6.30"},{"v":8.5,"d":"8.50"},{"v":10.9,"d":"10.90"},{"v":15.3,"d":"15.30"},{"v":20,"d":"20.00"},{"v":24,"d":"24.00"},{"v":23.7,"d":"23.70"},{"v":20,"d":"20.00"},{"v":14.1,"d":"14.10"},{"v":8.5,"d":"8.50"},{"v":5.3,"d":"5.30"}]
[null,"Alicante",{"$nulls":4},{"v":11.6,"d":"11.60"},{"v":12.4,"d":"12.40"},{"v":13.8,"d":"13.80"},{"v":15.7,"d":"15.70"},{"v":18.6,"d":"18.60"},{"v":22.2,"d":"22.20"},{"v":25,"d":"25.00"},{"v":25.5,"d":"25.50"},{"v":23.2,"d":"23.20"},{"v":19.1,"d":"19.10"},{"v":15,"d":"15.00"},{"v":12.1,"d":"12.10"}]
[null,"Almería",{"$nulls":4},{"v":12.4,"d":"12.40"},{"v":13,"d":"13.00"},{"v":14.4,"d":"14.40"},{"v":16.1,"d":"16.10"},{"v":18.7,"d":"18.70"},{"v":22.3,"d":"22.30"},{"v":25.5,"d":"25.50"},{"v":26,"d":"26.00"},{"v":24.1,"d":"24.10"},{"v":20.1,"d":"20.10"},{"v":16.2,"d":"16.20"},{"v":13.3,"d":"13.30"}]
[null,"Ávila",{"$nulls":4},{"v":3.1,"d":"3.10"},{"v":4,"d":"4.00"},{"v":5.6,"d":"5.60"},{"v":7.6,"d":"7.60"},{"v":11.5,"d":"11.50"},{"v":16,"d":"16.00"},{"v":19.9,"d":"19.90"},{"v":19.4,"d":"19.40"},{"v":16.5,"d":"16.50"},{"v":11.2,"d":"11.20"},{"v":6,"d":"6.00"},{"v":3.4,"d":"3.40"}]
[null,"Badajoz",{"$nulls":4},{"v":8.7,"d":"8.70"},{"v":10.1,"d":"10.10"},{"v":12,"d":"12.00"},{"v":14.2,"d":"14.20"},{"v":17.9,"d":"17.90"},{"v":22.3,"d":"22.30"},{"v":25.3,"d":"25.30"},{"v":25,"d":"25.00"},{"v":22.6,"d":"22.60"},{"v":17.4,"d":"17.40"},{"v":12.1,"d":"12.10"},{"v":9,"d":"9.00"}]
[null,"Barcelona",{"$nulls":4},{"v":8.8,"d":"8.80"},{"v":9.5,"d":"9.50"},{"v":11.1,"d":"11.10"},{"v":12.8,"d":"12.80"},{"v":16,"d":"16.00"},{"v":19.7,"d":"19.70"},{"v":22.9,"d":"22.90"},{"v":23,"d":"23.00"},{"v":21,"d":"21.00"},{"v":17.1,"d":"17.10"},{"v":12.5,"d":"12.50"},{"v":9.6,"d":"9.60"}]
[null,"Bilbao",{"$nulls":4},{"v":8.9,"d":"8.90"},{"v":9.6,"d":"9.60"},{"v":10.4,"d":"10.40"},{"v":11.8,"d":"11.80"},{"v":14.6,"d":"14.60"},{"v":17.4,"d":"17.40"},{"v":19.7,"d":"19.70"},{"v":19.8,"d":"19.80"},{"v":18.8,"d":"18.80"},{"v":16,"d":"16.00"},{"v":11.8,"d":"11.80"},{"v":9.5,"d":"9.50"}]
[null,"Burgos",{"$nulls":4},{"v":2.6,"d":"2.60"},{"v":3.9,"d":"3.90"},{"v":5.7,"d":"5.70"},{"v":7.6,"d":"7.60"},{"v":11.2,"d":"11.20"},{"v":15,"d":"15.00"},{"v":18.4,"d":"18.40"},{"v":18.3,"d":"18.30"},{"v":15.8,"d":"15.80"},{"v":11.1,"d":"11.10"},{"v":5.8,"d":"5.80"},{"v":3.2,"d":"3.20"}]
[null,"Cáceres",{"$nulls":4},{"v":7.8,"d":"7.80"},{"v":9.3,"d":"9.30"},{"v":11.7,"d":"11.70"},{"v":13,"d":"13.00"},{"v":16.6,"d":"16.60"},{"v":22.3,"d":"22.30"},{"v":26.1,"d":"26.10"},{"v":25.4,"d":"25.40"},{"v":23.6,"d":"23.60"},{"v":17.4,"d":"17.40"},{"v":12,"d":"12.00"},{"v":8.8,"d":"8.80"}]
[null,"Cádiz",{"$nulls":4},{"v":12.8,"d":"12.80"},{"v":13.5,"d":"13.50"},{"v":14.7,"d":"14.70"},{"v":16.2,"d":"16.20"},{"v":18.7,"d":"18.70"},{"v":21.5,"d":"21.50"},{"v":24,"d":"24.00"},{"v":24.5,"d":"24.50"},{"v":23.5,"d":"23.50"},{"v":20.1,"d":"20.10"},{"v":16.1,"d":"16.10"},{"v":13.3,"d":"13.30"}]
[null,"Castellón",{"$nulls":4},{"v":10.1,"d":"10.10"},{"v":11.1,"d":"11.10"},{"v":12.7,"d":"12.70"},{"v":14.2,"d":"14.20"},{"v":17.2,"d":"17.20"},{"v":21.3,"d":"21.30"},{"v":24.1,"d":"24.10"},{"v":24.5,"d":"24.50"},{"v":22.3,"d":"22.30"},{"v":18.3,"d":"18.30"},{"v":13.5,"d":"13.50"},{"v":11.2,"d":"11.20"}]
[null,"Ceuta",{"$nulls":4},{"v":11.5,"d":"11.50"},{"v":11.6,"d":"11.60"},{"v":12.6,"d":"12.60"},{"v":13.9,"d":"13.90"},{"v":16.3,"d":"16.30"},{"v":18.8,"d":"18.80"},{"v":21.7,"d":"21.70"},{"v":22.2,"d":"22.20"},{"v":20.2,"d":"20.20"},{"v":17.7,"d":"17.70"},{"v":14.1,"d":"14.10"},{"v":12.1,"d":"12.10"}]
[null,"Ciudad Real",{"$nulls":4},{"v":5.7,"d":"5.70"},{"v":7.2,"d":"7.20"},{"v":9.6,"d":"9.60"},{"v":11.9,"d":"11.90"},{"v":16,"d":"16.00"},{"v":20.8,"d":"20.80"},{"v":25,"d":"25.00"},{"v":24.7,"d":"24.70"},{"v":21,"d":"21.00"},{"v":14.8,"d":"14.80"},{"v":9.1,"d":"9.10"},{"v":5.9,"d":"5.90"}]
[null,"Córdoba",{"$nulls":4},{"v":9.5,"d":"9.50"},{"v":10.9,"d":"10.90"},{"v":13.1,"d":"13.10"},{"v":15.2,"d":"15.20"},{"v":19.2,"d":"19.20"},{"v":23.1,"d":"23.10"},{"v":26.9,"d":"26.90"},{"v":26.7,"d":"26.70"},{"v":23.7,"d":"23.70"},{"v":18.4,"d":"18.40"},{"v":12.9,"d":"12.90"},{"v":9.7,"d":"9.70"}]
[null,"Coruña, La",{"$nulls":4},{"v":10.2,"d":"10.20"},{"v":10.5,"d":"10.50"},{"v":11.3,"d":"11.30"},{"v":12.1,"d":"12.10"},{"v":14.1,"d":"14.10"},{"v":16.4,"d":"16.40"},{"v":18.4,"d":"18.40"},{"v":18.9,"d":"18.90"},{"v":18.1,"d":"18.10"},{"v":15.7,"d":"15.70"},{"v":12.7,"d":"12.70"},{"v":10.9,"d":"10.90"}]
[null,"Cuenca",{"$nulls":4},{"v":4.2,"d":"4.20"},{"v":5.2,"d":"5.20"},{"v":7.4,"d":"7.40"},{"v":9.6,"d":"9.60"},{"v":13.6,"d":"13.60"},{"v":18.2,"d":"18.20"},{"v":22.4,"d":"22.40"},{"v":22.1,"d":"22.10"},{"v":18.6,"d":"18.60"},{"v":12.9,"d":"12.90"},{"v":7.6,"d":"7.60"},{"v":4.8,"d":"4.80"}]
[null,"Gerona",{"$nulls":4},{"v":6.8,"d":"6.80"},{"v":7.9,"d":"7.90"},{"v":9.8,"d":"9.80"},{"v":11.6,"d":"11.60"},{"v":15.4,"d":"15.40"},{"v":19.4,"d":"19.40"},{"v":22.8,"d":"22.80"},{"v":22.4,"d":"22.40"},{"v":19.9,"d":"19.90"},{"v":15.2,"d":"15.20"},{"v":10.2,"d":"10.20"},{"v":7.7,"d":"7.70"}]
[null,"Granada",{"$nulls":4},{"v":6.5,"d":"6.50"},{"v":8.4,"d":"8.40"},{"v":10.5,"d":"10.50"},{"v":12.4,"d":"12.40"},{"v":16.3,"d":"16.30"},{"v":21.1,"d":"21.10"},{"v":24.3,"d":"24.30"},{"v":24.1,"d":"24.10"},{"v":21.1,"d":"21.10"},{"v":15.4,"d":"15.40"},{"v":10.6,"d":"10.60"},{"v":7.4,"d":"7.40"}]
[null,"Guadalajara",{"$nulls":4},{"v":5.5,"d":"5.50"},{"v":6.8,"d":"6.80"},{"v":8.8,"d":"8.80"},{"v":11.6,"d":"11.60"},{"v":15.3,"d":"15.30"},{"v":19.8,"d":"19.80"},{"v":23.5,"d":"23.50"},{"v":22.8,"d":"22.80"},{"v":19.5,"d":"19.50"},{"v":14.1,"d":"14.10"},{"v":9,"d":"9.00"},{"v":5.9,"d":"5.90"}]
[null,"Huelva",{"$nulls":4},{"v":12.2,"d":"12.20"},{"v":12.8,"d":"12.80"},{"v":14.4,"d":"14.40"},{"v":16.5,"d":"16.50"},{"v":19.2,"d":"19.20"},{"v":22.2,"d":"22.20"},{"v":25.3,"d":"25.30"},{"v":25.7,"d":"25.70"},{"v":23.7,"d":"23.70"},{"v":20,"d":"20.00"},{"v":15.4,"d":"15.40"},{"v":12.5,"d":"12.50"}]
[null,"Huesca",{"$nulls":4},{"v":4.7,"d":"4.70"},{"v":6.7,"d":"6.70"},{"v":9,"d":"9.00"},{"v":11.3,"d":"11.30"},{"v":15.3,"d":"15.30"},{"v":19.5,"d":"19.50"},{"v":23.3,"d":"23.30"},{"v":22.7,"d":"22.70"},{"v":19.7,"d":"19.70"},{"v":14.6,"d":"14.60"},{"v":8.7,"d":"8.70"},{"v":5.3,"d":"5.30"}]
[null,"Jaén",{"$nulls":4},{"v":8.7,"d":"8.70"},{"v":9.9,"d":"9.90"},{"v":12,"d":"12.00"},{"v":14.3,"d":"14.30"},{"v":18.5,"d":"18.50"},{"v":23.1,"d":"23.10"},{"v":27.2,"d":"27.20"},{"v":27.1,"d":"27.10"},{"v":23.6,"d":"23.60"},{"v":17.6,"d":"17.60"},{"v":12.2,"d":"12.20"},{"v":8.7,"d":"8.70"}]
[null,"León",{"$nulls":4},{"v":3.1,"d":"3.10"},{"v":4.4,"d":"4.40"},{"v":6.6,"d":"6.60"},{"v":8.6,"d":"8.60"},{"v":12.1,"d":"12.10"},{"v":16.4,"d":"16.40"},{"v":19.7,"d":"19.70"},{"v":19.1,"d":"19.10"},{"v":16.7,"d":"16.70"},{"v":11.7,"d":"11.70"},{"v":6.8,"d":"6.80"},{"v":3.8,"d":"3.80"}]
[null,"Lleida",{"$nulls":4},{"v":5.5,"d":"5.50"},{"v":7.8,"d":"7.80"},{"v":10.3,"d":"10.30"},{"v":13,"d":"13.00"},{"v":17.1,"d":"17.10"},{"v":21.2,"d":"21.20"},{"v":24.6,"d":"24.60"},{"v":24,"d":"24.00"},{"v":21.1,"d":"21.10"},{"v":15.7,"d":"15.70"},{"v":9.2,"d":"9.20"},{"v":5.8,"d":"5.80"}]
[null,"Logroño",{"$nulls":4},{"v":5.8,"d":"5.80"},{"v":7.3,"d":"7.30"},{"v":9.4,"d":"9.40"},{"v":11.5,"d":"11.50"},{"v":15.1,"d":"15.10"},{"v":19,"d":"19.00"},{"v":22.2,"d":"22.20"},{"v":21.8,"d":"21.80"},{"v":19.2,"d":"19.20"},{"v":14.4,"d":"14.40"},{"v":9.1,"d":"9.10"},{"v":6.3,"d":"6.30"}]
[null,"Lugo",{"$nulls":4},{"v":5.8,"d":"5.80"},{"v":6.5,"d":"6.50"},{"v":7.8,"d":"7.80"},{"v":9.5,"d":"9.50"},{"v":11.7,"d":"11.70"},{"v":14.9,"d":"14.90"},{"v":17.2,"d":"17.20"},{"v":17.5,"d":"17.50"},{"v":16,"d":"16.00"},{"v":12.5,"d":"12.50"},{"v":8.6,"d":"8.60"},{"v":6.3,"d":"6.30"}]
[null,"Madrid",{"$nulls":4},{"v":6.2,"d":"6.20"},{"v":7.4,"d":"7.40"},{"v":9.9,"d":"9.90"},{"v":12.2,"d":"12.20"},{"v":16,"d":"16.00"},{"v":20.7,"d":"20.70"},{"v":24.4,"d":"24.40"},{"v":23.9,"d":"23.90"},{"v":20.5,"d":"20.50"},{"v":14.7,"d":"14.70"},{"v":9.4,"d":"9.40"},{"v":6.4,"d":"6.40"}]
[null,"Málaga",{"$nulls":4},{"v":12.2,"d":"12.20"},{"v":12.8,"d":"12.80"},{"v":14,"d":"14.00"},{"v":15.8,"d":"15.80"},{"v":18.7,"d":"18.70"},{"v":22.1,"d":"22.10"},{"v":24.7,"d":"24.70"},{"v":25.3,"d":"25.30"},{"v":23.1,"d":"23.10"},{"v":19.1,"d":"19.10"},{"v":15.1,"d":"15.10"},{"v":12.6,"d":"12.60"}]
[null,"Melilla",{"$nulls":4},{"v":13.2,"d":"13.20"},{"v":13.8,"d":"13.80"},{"v":14.6,"d":"14.60"},{"v":15.9,"d":"15.90"},{"v":18.3,"d":"18.30"},{"v":21.5,"d":"21.50"},{"v":24.4,"d":"24.40"},{"v":25.3,"d":"25.30"},{"v":23.5,"d":"23.50"},{"v":20,"d":"20.00"},{"v":16.6,"d":"16.60"},{"v":14.1,"d":"14.10"}]
[null,"Murcia",{"$nulls":4},{"v":10.6,"d":"10.60"},{"v":11.4,"d":"11.40"},{"v":12.6,"d":"12.60"},{"v":14.5,"d":"14.50"},{"v":17.4,"d":"17.40"},{"v":21,"d":"21.00"},{"v":23.9,"d":"23.90"},{"v":24.6,"d":"24.60"},{"v":22.5,"d":"22.50"},{"v":18.7,"d":"18.70"},{"v":14.3,"d":"14.30"},{"v":11.3,"d":"11.30"}]
[null,"Orense",{"$nulls":4},{"v":7.4,"d":"7.40"},{"v":9.3,"d":"9.30"},{"v":10.7,"d":"10.70"},{"v":12.4,"d":"12.40"},{"v":15.3,"d":"15.30"},{"v":19.3,"d":"19.30"},{"v":21.9,"d":"21.90"},{"v":21.7,"d":"21.70"},{"v":19.8,"d":"19.80"},{"v":15,"d":"15.00"},{"v":10.6,"d":"10.60"},{"v":8.2,"d":"8.20"}]
[null,"Oviedo",{"$nulls":4},{"v":7.5,"d":"7.50"},{"v":8.5,"d":"8.50"},{"v":9.5,"d":"9.50"},{"v":10.3,"d":"10.30"},{"v":12.8,"d":"12.80"},{"v":15.8,"d":"15.80"},{"v":18,"d":"18.00"},{"v":18.3,"d":"18.30"},{"v":17.4,"d":"17.40"},{"v":14,"d":"14.00"},{"v":10.4,"d":"10.40"},{"v":8.7,"d":"8.70"}]
[null,"Palencia",{"$nulls":4},{"v":4.1,"d":"4.10"},{"v":5.6,"d":"5.60"},{"v":7.5,"d":"7.50"},{"v":9.5,"d":"9.50"},{"v":13,"d":"13.00"},{"v":17.2,"d":"17.20"},{"v":20.7,"d":"20.70"},{"v":20.3,"d":"20.30"},{"v":17.9,"d":"17.90"},{"v":13,"d":"13.00"},{"v":7.6,"d":"7.60"},{"v":4.4,"d":"4.40"}]
[null,"Palma de Mallorca",{"$nulls":4},{"v":11.6,"d":"11.60"},{"v":11.8,"d":"11.80"},{"v":12.9,"d":"12.90"},{"v":14.7,"d":"14.70"},{"v":17.6,"d":"17.60"},{"v":21.8,"d":"21.80"},{"v":24.6,"d":"24.60"},{"v":25.3,"d":"25.30"},{"v":23.5,"d":"23.50"},{"v":20,"d":"20.00"},{"v":15.6,"d":"15.60"},{"v":13,"d":"13.00"}]
[null,"Pamplona",{"$nulls":4},{"v":4.5,"d":"4.50"},{"v":6.5,"d":"6.50"},{"v":8,"d":"8.00"},{"v":9.9,"d":"9.90"},{"v":13.3,"d":"13.30"},{"v":17.3,"d":"17.30"},{"v":20.5,"d":"20.50"},{"v":20.3,"d":"20.30"},{"v":18.2,"d":"18.20"},{"v":13.7,"d":"13.70"},{"v":8.3,"d":"8.30"},{"v":5.7,"d":"5.70"}]
[null,"Pontevedra",{"$nulls":4},{"v":9.9,"d":"9.90"},{"v":10.7,"d":"10.70"},{"v":11.9,"d":"11.90"},{"v":13.6,"d":"13.60"},{"v":15.4,"d":"15.40"},{"v":18.8,"d":"18.80"},{"v":20.7,"d":"20.70"},{"v":20.5,"d":"20.50"},{"v":19.1,"d":"19.10"},{"v":16.1,"d":"16.10"},{"v":12.6,"d":"12.60"},{"v":10.3,"d":"10.30"}]
[null,"Salamanca",{"$nulls":4},{"v":3.7,"d":"3.70"},{"v":5.3,"d":"5.30"},{"v":7.3,"d":"7.30"},{"v":9.6,"d":"9.60"},{"v":13.4,"d":"13.40"},{"v":17.8,"d":"17.80"},{"v":21,"d":"21.00"},{"v":20.3,"d":"20.30"},{"v":17.5,"d":"17.50"},{"v":12.3,"d":"12.30"},{"v":7,"d":"7.00"},{"v":4.1,"d":"4.10"}]
[null,"San Sebastian",{"$nulls":4},{"v":7.9,"d":"7.90"},{"v":8.5,"d":"8.50"},{"v":9.4,"d":"9.40"},{"v":10.7,"d":"10.70"},{"v":13.5,"d":"13.50"},{"v":16.1,"d":"16.10"},{"v":18.4,"d":"18.40"},{"v":18.7,"d":"18.70"},{"v":18,"d":"18.00"},{"v":15.2,"d":"15.20"},{"v":10.9,"d":"10.90"},{"v":8.6,"d":"8.60"}]
[null,"Santander",{"$nulls":4},{"v":9.7,"d":"9.70"},{"v":10.3,"d":"10.30"},{"v":10.8,"d":"10.80"},{"v":11.9,"d":"11.90"},{"v":14.3,"d":"14.30"},{"v":17,"d":"17.00"},{"v":19.3,"d":"19.30"},{"v":19.5,"d":"19.50"},{"v":18.5,"d":"18.50"},{"v":16.1,"d":"16.10"},{"v":12.5,"d":"12.50"},{"v":10.5,"d":"10.50"}]
[null,"Segovia",{"$nulls":4},{"v":4.1,"d":"4.10"},{"v":5.2,"d":"5.20"},{"v":7.1,"d":"7.10"},{"v":9.1,"d":"9.10"},{"v":13.1,"d":"13.10"},{"v":17.7,"d":"17.70"},{"v":21.6,"d":"21.60"},{"v":21.2,"d":"21.20"},{"v":17.9,"d":"17.90"},{"v":12.6,"d":"12.60"},{"v":7.3,"d":"7.30"},{"v":4.3,"d":"4.30"}]
[null,"Sevilla",{"$nulls":4},{"v":10.7,"d":"10.70"},{"v":11.9,"d":"11.90"},{"v":14,"d":"14.00"},{"v":16,"d":"16.00"},{"v":19.6,"d":"19.60"},{"v":23.4,"d":"23.40"},{"v":26.8,"d":"26.80"},{"v":26.8,"d":"26.80"},{"v":24.4,"d":"24.40"},{"v":19.5,"d":"19.50"},{"v":14.3,"d":"14.30"},{"v":11.1,"d":"11.10"}]
[null,"Soria",{"$nulls":4},{"v":2.9,"d":"2.90"},{"v":4,"d":"4.00"},{"v":5.8,"d":"5.80"},{"v":8,"d":"8.00"},{"v":11.8,"d":"11.80"},{"v":16.1,"d":"16.10"},{"v":19.9,"d":"19.90"},{"v":19.5,"d":"19.50"},{"v":16.5,"d":"16.50"},{"v":11.3,"d":"11.30"},{"v":6.1,"d":"6.10"},{"v":3.4,"d":"3.40"}]
[null,"Tarragona",{"$nulls":4},{"v":10,"d":"10.00"},{"v":11.3,"d":"11.30"},{"v":13.1,"d":"13.10"},{"v":15.3,"d":"15.30"},{"v":18.4,"d":"18.40"},{"v":22.2,"d":"22.20"},{"v":25.3,"d":"25.30"},{"v":25.3,"d":"25.30"},{"v":22.7,"d":"22.70"},{"v":18.4,"d":"18.40"},{"v":13.5,"d":"13.50"},{"v":10.7,"d":"10.70"}]
[null,"Teruel",{"$nulls":4},{"v":3.8,"d":"3.80"},{"v":4.8,"d":"4.80"},{"v":6.8,"d":"6.80"},{"v":9.3,"d":"9.30"},{"v":12.6,"d":"12.60"},{"v":17.5,"d":"17.50"},{"v":21.3,"d":"21.30"},{"v":20.6,"d":"20.60"},{"v":17.9,"d":"17.90"},{"v":12.1,"d":"12.10"},{"v":7,"d":"7.00"},{"v":4.5,"d":"4.50"}]
[null,"Toledo",{"$nulls":4},{"v":6.1,"d":"6.10"},{"v":8.1,"d":"8.10"},{"v":10.9,"d":"10.90"},{"v":12.8,"d":"12.80"},{"v":16.8,"d":"16.80"},{"v":22.5,"d":"22.50"},{"v":26.5,"d":"26.50"},{"v":25.7,"d":"25.70"},{"v":22.6,"d":"22.60"},{"v":16.2,"d":"16.20"},{"v":10.7,"d":"10.70"},{"v":7.1,"d":"7.10"}]
[null,"Valencia",{"$nulls":4},{"v":10.4,"d":"10.40"},{"v":11.4,"d":"11.40"},{"v":12.6,"d":"12.60"},{"v":14.5,"d":"14.50"},{"v":17.4,"d":"17.40"},{"v":21.1,"d":"21.10"},{"v":24,"d":"24.00"},{"v":24.5,"d":"24.50"},{"v":22.3,"d":"22.30"},{"v":18.3,"d":"18.30"},{"v":13.7,"d":"13.70"},{"v":10.9,"d":"10.90"}]
[null,"Valladolid",{"$nulls":4},{"v":4.1,"d":"4.10"},{"v":6.1,"d":"6.10"},{"v":8.1,"d":"8.10"},{"v":9.9,"d":"9.90"},{"v":13.3,"d":"13.30"},{"v":18,"d":"18.00"},{"v":21.5,"d":"21.50"},{"v":21.3,"d":"21.30"},{"v":18.6,"d":"18.60"},{"v":12.9,"d":"12.90"},{"v":7.6,"d":"7.60"},{"v":4.8,"d":"4.80"}]
[null,"Vitoria",{"$nulls":4},{"v":4.6,"d":"4.60"},{"v":6,"d":"6.00"},{"v":7.2,"d":"7.20"},{"v":9.2,"d":"9.20"},{"v":12.4,"d":"12.40"},{"v":15.6,"d":"15.60"},{"v":18.3,"d":"18.30"},{"v":18.5,"d":"18.50"},{"v":16.5,"d":"16.50"},{"v":12.7,"d":"12.70"},{"v":7.5,"d":"7.50"},{"v":5,"d":"5.00"}]
[null,"Zamora",{"$nulls":4},{"v":4.3,"d":"4.30"},{"v":6.3,"d":"6.30"},{"v":8.3,"d":"8.30"},{"v":10.5,"d":"10.50"},{"v":14,"d":"14.00"},{"v":18.5,"d":"18.50"},{"v":21.8,"d":"21.80"},{"v":21.3,"d":"21.30"},{"v":18.7,"d":"18.70"},{"v":13.4,"d":"13.40"},{"v":8.1,"d":"8.10"},{"v":4.9,"d":"4.90"}]
[null,"Zaragoza",{"$nulls":4},{"v":6.2,"d":"6.20"},{"v":8,"d":"8.00"},{"v":10.3,"d":"10.30"},{"v":12.8,"d":"12.80"},{"v":16.8,"d":"16.80"},{"v":21,"d":"21.00"},{"v":24.3,"d":"24.30"},{"v":23.8,"d":"23.80"},{"v":20.7,"d":"20.70"},{"v":15.4,"d":"15.40"},{"v":9.7,"d":"9.70"},{"v":6.5,"d":"6.50"}]
[null,"Palmas de Gran Canarias",{"$nulls":4},{"v":17.5,"d":"17.50"},{"v":17.6,"d":"17.60"},{"v":18.3,"d":"18.30"},{"v":18.7,"d":"18.70"},{"v":19.9,"d":"19.90"},{"v":21.4,"d":"21.40"},{"v":23.2,"d":"23.20"},{"v":24,"d":"24.00"},{"v":23.9,"d":"23.90"},{"v":22.5,"d":"22.50"},{"v":20.4,"d":"20.40"},{"v":18.3,"d":"18.30"}]
[null,"Santa Cruz de Tenerife",{"$nulls":4},{"v":17.9,"d":"17.90"},{"v":18,"d":"18.00"},{"v":18.6,"d":"18.60"},{"v":19.1,"d":"19.10"},{"v":20.5,"d":"20.50"},{"v":22.2,"d":"22.20"},{"v":24.6,"d":"24.60"},{"v":25.1,"d":"25.10"},{"v":24.4,"d":"24.40"},{"v":22.4,"d":"22.40"},{"v":20.7,"d":"20.70"},{"v":18.8,"d":"18.80"}]

{"sheet":"Datos SOLAR","index":21,"n_rows":120,"n_cols":15,"rows_kept":120,"hidden":true,"merged":[[1,1,1,13],[11,1,11,13],[66,1,66,13]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":2}
[]
[null,"DATOS RADIACIÓN SOLAR"]
[]
[null,"Localidad","Madrid",null,"Rad anual",17.593376]
[null,null,2,3,4,5,6,7,8,9,10,11,12,13]
[null,null,"ENERO ","FEBRERO","MARZO","ABRIL","MAYO","JUNIO","JULIO","AGOSTO","SEPTIEMBRE","OCTUBRE","NOVIEMBRE","DICIEMBRE"]
[null,"Atlas Radiacion solar 2012 AEMET",{"v":8.183804,"d":"8.18"},{"v":11.716899999999999,"d":"11.72"},{"v":16.76418,"d":"16.76"},{"v":20.7299,"d":"20.73"},{"v":23.79432,"d":"23.79"},{"v":27.904248,"d":"27.90"},{"v":28.985807999999995,"d":"28.99"},{"v":25.2364,"d":"25.24"},{"v":19.720444,"d":"19.72"},{"v":12.834512,"d":"12.83"},{"v":8.760636,"d":"8.76"},{"v":6.7417240000000005,"d":"6.74"}]
[null,"Pliego Instalaciones solar térmica IDAE",{"v":6.7,"d":"6.70"},{"v":10.6,"d":"10.60"},{"v":13.6,"d":"13.60"},{"v":18.8,"d":"18.80"},{"v":20.9,"d":"20.90"},{"v":23.5,"d":"23.50"},{"v":26,"d":"26.00"},{"v":23.1,"d":"23.10"},{"v":16.9,"d":"16.90"},{"v":11.4,"d":"11.40"},{"v":7.5,"d":"7.50"},{"v":5.9,"d":"5.90"}]
[null,"Base de datos PvGis"]
[null,"Otra localidad (definida por usuario)"]
[]
[null,"Energía en megajulios que incide sobre un metro cuadrado de superficie horizontal en un día medio de cada mes. (Fuente: CENSOLAR)."]
[null,null," ENE  "," FEB  "," MAR  "," ABR  "," MAY  "," JUN  "," JUL  "," AGO  "," SEP  "," OCT  "," NOV  "," DIC  "]
[null,"Vitoria",4.6,6.9,11.2,13,14.8,16.6,18.1,17.3,14.3,9.5,5.5,4.1]
[null,"Albacete",6.7,10.5,15,19.2,21.2,25.1,26.7,23.2,18.8,12.4,8.4,6.4]
[null,"Alicante",8.5,12,16.3,18.9,23.1,24.8,25.8,22.5,18.3,13.6,9.8,7.6]
[null,"Almería",8.9,12.2,16.4,19.6,23.1,24.6,25.3,22.5,18.5,13.9,10,8]
[null,"Oviedo",5.3,7.7,10.6,12.2,15,15.2,16.8,14.8,12.4,9.8,5.9,4.6]
[null,"Ávila",6,9.1,13.5,17.7,19.4,22.3,26.3,25.3,18.8,11.2,6.9,5.2]
[null,"Badajoz",6.5,10,13.6,18.7,21.8,24.6,25.9,23.8,17.9,12.3,8.2,6.2]
[null,"Palma de Mallorca",7.2,10.7,14.4,16.2,21,22.7,24.2,20.6,16.4,12.1,8.5,6.5]
[null,"Barcelona",6.5,9.5,12.9,16.1,18.6,20.3,21.6,18.1,14.6,10.8,7.2,5.8]
[null,"Burgos",5.1,7.9,12.4,16,18.7,21.5,23,20.7,16.7,10.1,6.5,4.5]
[null,"Cáceres",6.8,10,14.7,19.6,22.1,25.1,28.1,25.4,19.7,12.7,8.9,6.6]
[null,"Cádiz",8.1,11.5,15.7,18.5,22.2,23.8,25.9,23,18.1,14.2,10,7.4]
[null,"Santander",5,7.4,11,13,16.1,17,18.4,15.5,13,9.5,5.8,4.5]
[null,"Castellón",8,12.2,15.5,17.4,20.6,21.4,23.9,19.5,16.6,13.1,8.6,7.3]
[null,"Ceuta",8.9,13.1,18.6,21,24.3,26.7,26.8,24.3,19.1,14.2,11,8.6]
[null,"Ciudad Real",7,10.1,15,18.7,21.4,23.7,25.3,23.2,18.8,12.5,8.7,6.5]
[null,"Córdoba",7.2,10.1,15.1,18.5,21.8,25.9,28.5,25.1,19.9,12.6,8.6,6.9]
[null,"Coruña, La",5.4,8,11.4,12.4,15.4,16.2,17.4,15.3,13.9,10.9,6.4,5.1]
[null,"Cuenca",5.9,8.8,12.9,17.4,18.7,22,25.6,22.3,17.5,11.2,7.2,5.5]
[null,"Gerona",7.1,10.5,14.2,15.9,18.7,19,22.3,18.5,14.9,11.7,7.8,6.6]
[null,"Granada",7.8,10.8,15.2,18.5,21.9,24.8,26.7,23.6,18.8,12.9,9.6,7.1]
[null,"Guadalajara",6.5,9.2,14,17.9,19.4,22.7,25,23.2,17.8,11.7,7.8,5.6]
[null,"Bilbao",5.5,7.7,11.3,11.7,14.6,16.2,16.1,13.6,12.7,10.3,6.2,5]
[null,"Huelva",7.6,11.3,16,19.5,24.1,25.6,28.7,25.6,21.2,14.5,9.2,7.5]
[null,"Huesca",6.1,9.6,14.3,18.7,20.3,22.1,23.1,20.9,16.9,11.3,7.2,5.1]
[null,"Jaén",6.7,10.1,14.4,18,20.3,24.4,26.7,24.1,19.2,11.9,8.1,6.5]
[null,"Palmas de Gran Canarias",11.2,14.2,17.8,19.6,21.7,22.5,24.3,21.9,19.8,15.1,12.3,10.7]
[null,"León",5.8,8.7,13.8,17.2,19.5,22.1,24.2,20.9,17.2,10.4,7,4.8]
[null,"Lleida",6,9.9,18,18.8,20.9,22.6,23.8,21.3,16.8,12.1,7.2,4.8]
[null,"Lugo",5.1,7.6,11.7,15.2,17.1,19.5,20.2,18.4,15,9.9,6.2,4.5]
[null,"Madrid",6.7,10.6,13.6,18.8,20.9,23.5,26,23.1,16.9,11.4,7.5,5.9]
[null,"Málaga",8.3,12,15.5,18.5,23.2,24.5,26.5,23.2,19,13.6,9.3,8]
[null,"Melilla",9.4,12.6,17.2,20.3,23,24.8,24.8,22.6,18.3,14.2,10.9,8.7]
[null,"Murcia",10.1,14.8,16.6,20.4,24.2,25.6,27.7,23.5,18.6,13.9,9.8,8.1]
[null,"Pamplona",5,7.4,12.3,14.5,17.1,18.9,20.5,18.2,16.2,10.2,6,4.5]
[null,"Orense",4.7,7.3,11.3,14,16.2,17.6,18.3,16.6,14.3,9.4,5.6,4.3]
[null,"Palencia",5.3,9,13.2,17.5,19.7,21.8,24.1,21.6,17.1,10.9,6.6,4.6]
[null,"Pontevedra",5.5,8.2,13,15.7,17.5,20.4,22,18.9,15.1,11.3,6.8,5.5]
[null,"Logroño",5.6,8.8,13.7,16.6,19.2,21.4,23.3,20.8,16.2,10.7,6.8,4.8]
[null,"Salamanca",6.1,9.5,13.5,17.1,19.7,22.8,24.6,22.6,17.5,11.3,7.4,5.2]
[null,"Segovia",5.7,8.8,13.4,18.4,20.4,22.6,25.7,24.9,18.8,11.4,6.8,5.1]
[null,"Sevilla",7.3,10.9,14.4,19.2,22.4,24.3,24.9,23,17.9,12.3,8.8,6.9]
[null,"Soria",5.9,8.7,12.8,17.1,19.7,21.8,24.1,22.3,17.5,11.1,7.6,5.6]
[null,"Santa Cruz de Tenerife",10.7,13.3,18.1,21.5,25.7,26.5,29.3,26.6,21.2,16.2,10.8,9.3]
[null,"Tarragona",7.3,10.7,14.9,17.6,20.2,22.5,23.8,20.5,16.4,12.3,8.8,6.3]
[null,"Teruel",6.1,8.8,12.9,16.7,18.4,20.6,21.8,20.7,16.9,11,7.1,5.3]
[null,"Toledo",6.2,9.5,14,19.3,21,24.4,27.2,24.5,18.1,11.9,7.6,5.6]
[null,"Valencia",7.6,10.6,14.9,18.1,20.6,22.8,23.8,20.7,16.7,12,8.7,6.6]
[null,"Valladolid",5.5,8.8,13.9,17.2,19.9,22.6,25.1,23,18.3,11.2,6.9,4.2]
[null,"San Sebastian",5,7.1,10.8,12.7,15.5,16.7,17.9,15.7,13.1,9.3,6,4.6]
[null,"Zamora",5.4,8.9,13.2,17.3,22.2,21.6,23.5,22,17.2,11.1,6.7,4.6]
[null,"Zaragoza",6.3,9.8,15.2,18.3,21.8,24.2,25.1,23.4,18.3,12.1,7.4,5.7]
[]
[null,"Radiación global media diaria kWh/m2 dia.  Atlas  de radiación solaren España AEMET 2012.  Datos SAF 1983-2005"]
[null,null,"ENERO ","FEBRERO","MARZO","ABRIL","MAYO","JUNIO","JULIO","AGOSTO","SEPTIEMBRE","OCTUBRE","NOVIEMBRE","DICIEMBRE","anual"]
[null,"Albacete",2.49,3.39,4.72,5.97,6.65,7.65,7.96,6.91,5.51,3.75,2.64,2.11,4.98]
[null,"Alicante",2.61,3.49,{"v":4.7,"d":"4.70"},6.13,6.92,7.65,7.96,6.91,5.51,3.75,2.64,2.11,5.05]
[null,"Almería",2.84,3.72,4.93,6.52,7.21,7.94,7.89,7.02,5.71,4.15,3.02,2.46,5.29]
[null,"Ávila",2.13,3.06,4.44,5.45,6.15,7.31,7.72,6.66,5.17,3.37,2.29,1.81,4.63]
[null,"Badajoz",2.43,3.34,{"v":4.8,"d":"4.80"},5.84,{"v":6.8,"d":"6.80"},7.84,8.06,7.12,5.61,3.79,2.63,1.98,5.02]
[null,"Barcelona",2.18,3.14,4.34,5.69,6.47,{"v":7.1,"d":"7.10"},7.33,6.12,4.78,3.33,2.31,1.91,4.56]
[null,"Bilbao",1.56,2.23,3.43,{"v":4.3,"d":"4.30"},5.17,5.55,5.49,4.87,4.08,2.72,{"v":1.7,"d":"1.70"},1.38,3.54]
[null,"Burgos",1.69,2.55,4.08,4.96,6.04,7.22,7.42,6.44,4.96,3.05,1.92,1.45,4.31]
[null,"Cáceres",2.39,3.34,4.79,5.86,6.82,7.81,8.08,7.07,5.54,3.66,2.56,1.98,4.99]
[null,"Cádiz",2.77,3.71,5.03,6.37,7.29,{"v":7.9,"d":"7.90"},7.96,7.11,{"v":5.8,"d":"5.80"},4.13,2.96,2.38,5.28]
[null,"Castellón",2.43,3.34,4.53,5.88,6.52,7.24,7.48,6.38,5.03,3.63,2.55,2.08,4.76]
[null,"Ceuta",2.57,3.31,4.41,5.97,6.74,7.64,7.61,6.72,5.38,3.69,2.68,2.15,4.91]
[null,"Ciudad Real",2.36,3.39,4.85,5.92,{"v":6.7,"d":"6.70"},7.81,8.09,7.13,5.62,{"v":3.8,"d":"3.80"},2.61,2.01,5.03]
[null,"Córdoba",2.62,3.53,4.91,5.92,6.76,7.85,8.12,7.19,{"v":5.7,"d":"5.70"},3.88,2.79,2.23,5.12]
[null,"Coruña, La",{"v":1.6,"d":"1.60"},2.34,3.62,4.62,5.64,6.36,{"v":6.3,"d":"6.30"},5.71,4.39,2.71,1.74,1.34,3.86]
[null,"Cuenca",2.24,3.18,4.49,{"v":5.4,"d":"5.40"},6.26,7.44,7.85,6.83,{"v":5.3,"d":"5.30"},3.45,2.38,{"v":1.9,"d":"1.90"},4.73]
[null,"Gerona",2.14,3.04,4.27,5.29,5.99,6.56,7.03,5.93,4.71,3.25,2.27,1.86,4.36]
[null,"Granada",2.77,3.64,4.92,5.98,6.88,{"v":7.9,"d":"7.90"},8.07,7.18,5.73,4.05,2.92,2.37,{"v":5.2,"d":"5.20"}]
[null,"Guadalajara",{"v":2.2,"d":"2.20"},3.17,4.58,5.66,6.54,{"v":7.7,"d":"7.70"},7.95,6.96,5.41,3.52,2.34,1.85,4.82]
[null,"Huelva",2.69,3.63,4.97,6.12,7.01,7.92,8.07,{"v":7.2,"d":"7.20"},5.78,4.04,2.92,2.28,5.22]
[null,"Huesca",2.06,3.25,4.67,5.82,6.68,7.48,7.69,6.58,5.24,3.47,2.33,1.79,4.76]
[null,"Jaén",2.68,3.57,4.94,6.06,6.86,7.95,8.12,7.18,5.69,3.95,2.82,2.29,5.18]
[null,"León",1.86,2.86,4.28,5.35,6.21,7.39,7.58,6.57,4.99,3.13,2.09,1.56,4.49]
[null,"Lleida",1.98,3.25,4.73,6.03,6.81,{"v":7.6,"d":"7.60"},7.72,6.61,5.29,3.55,2.29,1.64,4.79]
[null,"Logroño",1.77,2.66,4.07,4.98,5.85,{"v":6.8,"d":"6.80"},7.05,6.13,4.76,3.07,1.97,1.54,4.22]
[null,"Lugo",1.65,2.37,3.64,4.49,5.32,6.27,6.33,5.71,4.35,2.71,1.79,{"v":1.4,"d":"1.40"},3.83]
[null,"Madrid",2.27,3.25,4.65,5.75,{"v":6.6,"d":"6.60"},7.74,8.04,{"v":7,"d":"7.00"},5.47,3.56,2.43,1.87,4.88]
[null,"Málaga",2.78,{"v":3.6,"d":"3.60"},4.85,6.15,{"v":7,"d":"7.00"},7.87,7.97,7.05,5.76,4.07,2.92,2.36,{"v":5.2,"d":"5.20"}]
[null,"Melilla",2.86,{"v":3.7,"d":"3.70"},4.82,6.32,6.76,7.29,7.35,6.66,5.55,4.13,3.04,2.57,5.09]
[null,"Murcia",2.72,{"v":3.6,"d":"3.60"},{"v":4.8,"d":"4.80"},6.29,6.96,7.73,7.89,6.87,5.51,3.99,2.88,2.35,5.13]
[null,"Orense",1.74,2.56,3.82,4.72,5.69,{"v":6.8,"d":"6.80"},6.96,6.18,4.66,2.87,1.84,1.44,4.11]
[null,"Oviedo",1.77,2.43,{"v":3.6,"d":"3.60"},4.46,4.99,5.34,5.29,{"v":4.8,"d":"4.80"},{"v":4.1,"d":"4.10"},2.74,1.87,1.49,3.57]
[null,"Palencia",1.89,2.96,4.44,5.46,6.38,7.51,7.72,6.74,5.19,3.29,2.14,1.61,4.61]
[null,"Palma de Mallorca",2.32,3.13,4.46,5.86,6.68,7.51,7.58,6.63,4.98,{"v":3.6,"d":"3.60"},{"v":2.5,"d":"2.50"},2.05,4.77]
[null,"Pamplona",1.62,2.49,{"v":3.8,"d":"3.80"},4.58,5.66,6.62,6.86,5.95,{"v":4.6,"d":"4.60"},2.96,1.87,1.47,4.04]
[null,"Pontevedra",1.74,2.53,3.82,4.76,5.77,6.73,6.76,6.05,4.64,{"v":2.9,"d":"2.90"},1.88,1.44,4.08]
[null,"Salamanca",2.08,3.09,4.49,5.56,6.44,{"v":7.6,"d":"7.60"},7.82,6.84,5.27,3.43,2.28,1.78,4.72]
[null,"San Sebastian",1.53,2.22,3.49,4.39,5.18,5.62,5.59,4.93,4.11,2.59,1.66,1.33,3.55]
[null,"Santander",{"v":1.6,"d":"1.60"},2.34,{"v":3.6,"d":"3.60"},{"v":4.6,"d":"4.60"},5.33,{"v":5.8,"d":"5.80"},5.71,5.04,4.18,2.69,1.69,1.36,3.66]
[null,"Segovia",{"v":2,"d":"2.00"},{"v":2.9,"d":"2.90"},4.32,5.26,6.09,{"v":7.3,"d":"7.30"},{"v":7.7,"d":"7.70"},6.67,5.15,3.29,2.16,1.72,4.55]
[null,"Sevilla",2.72,3.66,5.03,6.14,6.99,7.88,{"v":8.1,"d":"8.10"},{"v":7.2,"d":"7.20"},5.78,4.02,2.92,2.33,5.23]
[null,"Soria",1.96,2.92,4.33,5.27,6.12,7.15,7.48,6.43,4.98,3.23,2.16,1.72,4.48]
[null,"Tarragona",2.26,3.25,4.46,5.76,6.51,7.26,7.44,7.14,4.87,3.42,2.41,1.98,4.65]
[null,"Teruel",2.31,3.27,4.56,5.63,6.39,7.27,7.59,6.54,5.22,3.57,2.44,1.93,4.73]
[null,"Toledo",2.38,3.35,4.81,5.94,6.71,7.85,8.09,7.08,5.57,3.72,2.55,1.95,{"v":5,"d":"5.00"}]
[null,"Valencia",2.52,{"v":3.4,"d":"3.40"},4.68,6.07,6.78,7.48,7.68,6.62,5.28,3.78,2.67,2.13,4.92]
[null,"Valladolid",1.92,3.01,4.47,5.53,6.48,7.55,7.75,6.79,5.26,3.36,2.18,1.64,4.66]
[null,"Vitoria",1.56,2.32,3.58,4.46,{"v":5.4,"d":"5.40"},6.11,6.28,5.49,4.37,2.83,1.79,1.38,{"v":3.8,"d":"3.80"}]
[null,"Zamora",1.93,3.06,4.53,{"v":5.6,"d":"5.60"},6.53,7.67,{"v":7.8,"d":"7.80"},6.85,5.24,3.39,2.21,1.67,4.71]
[null,"Zaragoza",2.05,3.21,4.66,5.82,6.75,7.56,7.76,6.64,5.25,3.52,2.35,1.79,4.78]
[null,"Palmas de Gran Canarias",{"v":3.5,"d":"3.50"},4.14,5.03,5.95,6.51,6.22,6.06,6.05,5.64,{"v":4.7,"d":"4.70"},3.71,3.24,5.06]
[null,"Santa Cruz de Tenerife",3.47,4.22,5.04,6.11,6.59,7.22,{"v":7.6,"d":"7.60"},7.02,{"v":5.9,"d":"5.90"},4.79,{"v":3.7,"d":"3.70"},3.17,{"v":5.4,"d":"5.40"}]

{"sheet":"Factor K","index":22,"n_rows":238,"n_cols":23,"rows_kept":238,"hidden":true,"merged":[[2,2,2,22],[12,2,25,2],[27,2,40,2],[42,2,55,2],[57,2,70,2],[72,2,85,2],[87,2,100,2],[102,2,115,2],[117,2,130,2],[132,2,145,2],[147,2,160,2],[162,2,175,2],[177,2,190,2],[192,2,205,2],[207,2,220,2]],"read":"bin_skipped_in_rows","flags":["formulas_cached_only","records_skipped"],"rows_in_doubt":{"n":0,"rows":[]},"rows_in_doubt_other":32}
[]
[null,null,"Factor de corrección k para superficies inclinadas"]
[null,null,"Representa el cociente entre la energía total incidente en un día sobre una superficie orientada hacia el ecuador (sur en el hemisferio norte, norte en el hemisferio sur) e inclinada un determinado ángulo y y la energía total incidente en un día sobre una  superficie horizontal"]
[null,null,"Los valores están obtenidos del anexo X del Pliego de Condiciones Técnicas de Instalaciones de baja temperatura,  IDAE, 2002, tomados a su vez de CENSOLAR"]
[]
[null,null,"Provincia","Madrid",{"$nulls":3},"Localizacion factor K"]
[null,null,"Latitud",40.4,{"$nulls":4},"fila Enero",122]
[null,null,"Latitud (Redond)",40,{"$nulls":4},"columna",9]
[null,null,"Inclinación",40,null,"Enero","Febrero","Marzo","Abril","Mayo","Junio","Julio","Agosto","Septiembre","Octubre","Noviembre","Diciembre"," "]
[null,null,"Factor K",null,null,1.39,1.29,1.16,1.04,0.95,0.92,0.95,1.05,1.21,1.39,1.5,1.48]
[]
[28]
[null,1,{"v":28,"d":"latitud = 28 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,2,null,"Enero",{"v":1,"d":"1.00"},1.05,{"v":1.1,"d":"1.10"},1.14,1.17,{"v":1.2,"d":"1.20"},1.22,1.23,1.24,1.23,1.22,{"v":1.2,"d":"1.20"},1.18,1.14,{"v":1.1,"d":"1.10"},1.06,{"v":1,"d":"1.00"},0.94,0.88]
[null,3,null,"Febrero",{"v":1,"d":"1.00"},1.04,1.08,1.11,1.13,1.15,1.15,1.16,1.15,1.14,1.12,1.09,1.05,1.01,0.97,0.91,0.86,0.79,0.72]
[null,4,null,"Marzo",{"v":1,"d":"1.00"},1.03,1.05,1.07,1.08,1.08,1.07,1.06,1.04,1.01,0.98,0.94,{"v":0.9,"d":"0.90"},0.85,0.79,0.73,0.66,0.59,0.52]
[null,5,null,"Abril",{"v":1,"d":"1.00"},1.01,1.02,1.02,1.02,{"v":1,"d":"1.00"},0.98,0.96,0.92,0.89,0.84,0.79,0.73,0.67,0.61,0.54,0.47,0.39,0.32]
[null,6,null,"Mayo",{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},0.99,0.97,0.95,0.92,0.88,0.84,0.79,0.73,0.68,0.61,0.55,0.48,0.4,0.33,0.25,0.17]
[null,7,null,"Junio",{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},0.99,0.98,0.95,0.93,0.89,0.85,{"v":0.8,"d":"0.80"},0.75,0.69,0.63,0.57,{"v":0.5,"d":"0.50"},0.42,0.35,0.27,0.19,0.11]
[null,8,null,"Julio",{"v":1,"d":"1.00"}," ",{"v":1,"d":"1.00"},0.99,0.97,0.95,0.92,0.88,0.84,0.79,0.73,0.67,0.61,0.54,0.47,0.39,0.32,0.24,0.16]
[null,9,null,"Agosto",{"v":1,"d":"1.00"},1.02,1.02,1.03,1.02,1.01,0.99,0.96,0.93,0.89,0.84,0.79,0.73,0.67,{"v":0.6,"d":"0.60"},0.53,0.46,0.38,0.31]
[null,10,null,"Septiembre",{"v":1,"d":"1.00"},1.03,1.06,1.08,1.09,1.09,1.09,1.08,1.06,1.04,{"v":1,"d":"1.00"},0.96,0.92,0.86,0.81,0.74,0.67,{"v":0.6,"d":"0.60"},0.53]
[null,11,null,"Octubre",{"v":1,"d":"1.00"},1.05,{"v":1.1,"d":"1.10"},1.13,1.16,1.19,{"v":1.2,"d":"1.20"},1.21,1.21,{"v":1.2,"d":"1.20"},1.18,1.15,1.12,1.08,1.03,0.97,0.91,0.84,0.77]
[null,12,null,"Noviembre",{"v":1,"d":"1.00"},1.06,1.12,1.17,1.21,1.25,1.27,1.29,{"v":1.3,"d":"1.30"},{"v":1.3,"d":"1.30"},{"v":1.3,"d":"1.30"},1.28,1.26,1.22,1.18,1.14,1.08,1.02,0.95]
[null,13,null,"Diciembre",{"v":1,"d":"1.00"},1.06,1.12,1.17,1.21,1.24,1.27,1.29,{"v":1.3,"d":"1.30"},{"v":1.3,"d":"1.30"},{"v":1.3,"d":"1.30"},1.28,1.26,1.23,1.19,1.15,{"v":1.1,"d":"1.10"},1.04,0.98]
[null,14,null,"Media anual",{"v":1,"d":"1.00"},{"v":0.9458333333333334,"d":"0.95"},{"v":1.055,"d":"1.06"},{"v":1.0733333333333333,"d":"1.07"},{"v":1.0816666666666668,"d":"1.08"},{"v":1.0866666666666667,"d":"1.09"},{"v":1.080833333333333,"d":"1.08"},{"v":1.070833333333333,"d":"1.07"},{"v":1.0525,"d":"1.05"},{"v":1.0275,"d":"1.03"},{"v":0.9941666666666668,"d":"0.99"},{"v":0.9549999999999997,"d":"0.96"},{"v":0.9116666666666667,"d":"0.91"},0.86,{"v":0.8041666666666667,"d":"0.80"},{"v":0.7425,"d":"0.74"},{"v":0.6775000000000001,"d":"0.68"},{"v":0.6058333333333332,"d":"0.61"},{"v":0.535,"d":"0.54"}]
[29,15]
[null,16,{"v":29,"d":"latitud = 29 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,17,null,"Enero",{"v":1,"d":"1.00"},1.05,{"v":1.1,"d":"1.10"},1.15,1.18,1.21,1.23,1.24,1.25,1.24,1.23,1.22,1.19,1.16,1.12,1.07,1.02,0.96,{"v":0.9,"d":"0.90"}]
[null,18,null,"Febrero",{"v":1,"d":"1.00"},1.04,1.08,1.11,1.14,1.15,1.16,1.17,1.16,1.15,1.13,{"v":1.1,"d":"1.10"},1.07,1.03,0.98,0.93,0.87,0.81,0.74]
[null,19,null,"Marzo",{"v":1,"d":"1.00"},1.03,1.05,1.07,1.08,1.08,1.08,1.07,1.05,1.02,0.99,0.95,0.91,0.86,{"v":0.8,"d":"0.80"},0.74,0.68,0.61,0.54]
[null,20,null,"Abril",{"v":1,"d":"1.00"},1.02,1.02,1.03,1.02,1.01,0.99,0.97,0.93,{"v":0.9,"d":"0.90"},0.85,{"v":0.8,"d":"0.80"},0.75,0.69,0.62,0.55,0.48,0.41,0.33]
[null,21,null,"Mayo",{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},0.99,0.98,0.95,0.92,0.89,0.85,{"v":0.8,"d":"0.80"},0.75,0.69,0.63,0.56,0.49,0.42,0.34,0.26,0.18]
[null,22,null,"Junio",{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},0.99,0.98,0.96,0.93,{"v":0.9,"d":"0.90"},0.86,0.81,0.76,0.71,0.64,0.58,0.51,0.44,0.36,0.28,0.21,0.13]
[null,23,null,"Julio",{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},{"v":1,"d":"1.00"},0.99,0.98,0.95,0.92,0.89,0.85,{"v":0.8,"d":"0.80"},0.74,0.68,0.62,0.55,0.48,0.41,0.33,0.25,0.17]
[null,24,null,"Agosto",{"v":1,"d":"1.00"},1.02,1.03,1.03,1.03,1.01,{"v":1,"d":"1.00"},0.97,0.94,{"v":0.9,"d":"0.90"},0.85,{"v":0.8,"d":"0.80"},0.75,0.69,0.62,0.55,0.48,{"v":0.4,"d":"0.40"},0.32]
[null,25,null,"Septiembre",{"v":1,"d":"1.00"},1.03,1.06,1.08,{"v":1.1,"d":"1.10"},{"v":1.1,"d":"1.10"},{"v":1.1,"d":"1.10"},1.09,1.07,1.05,1.02,0.98,0.93,0.88,0.82,0.76,0.69,0.62,0.54]
[null,26,null,"Octubre",{"v":1,"d":"1.00"},1.05,{"v":1.1,"d":"1.10"},1.14,1.17,{"v":1.2,"d":"1.20"},1.21,1.22,1.22,1.21,1.19,1.17,1.14,{"v":1.1,"d":"1.10"},1.05,0.99,0.93,0.87,0.79]
[null,27,null,"Noviembre",{"v":1,"d":"1.00"},1.07,1.12,1.18,1.22,1.26,1.28,{"v":1.3,"d":"1.30"},1.32,1.32,1.31,{"v":1.3,"d":"1.30"},1.28,1.24,{"v":1.2,"d":"1.20"},1.16,{"v":1.1,"d":"1.10"},1.04,0.97]
[null,28,null,"Diciembre",{"v":1,"d":"1.00"},1.06,1.12,1.17,1.22,1.25,1.28,{"v":1.3,"d":"1.30"},1.31,1.32,1.31,{"v":1.3,"d":"1.30"},1.28,1.25,1.22,1.17,1.12,1.06,{"v":1,"d":"1.00"}]
[null,29,null,"Media anual",{"v":1,"d":"1.00"},{"v":1.0308333333333335,"d":"1.03"},{"v":1.0558333333333334,"d":"1.06"},{"v":1.0766666666666667,"d":"1.08"},1.09,{"v":1.0916666666666666,"d":"1.09"},{"v":1.0891666666666664,"d":"1.09"},{"v":1.0808333333333335,"d":"1.08"},{"v":1.0633333333333332,"d":"1.06"},{"v":1.0391666666666666,"d":"1.04"},{"v":1.0066666666666666,"d":"1.01"},{"v":0.9691666666666667,"d":"0.97"},{"v":0.9274999999999999,"d":"0.93"},{"v":0.8766666666666666,"d":"0.88"},{"v":0.8200000000000002,"d":"0.82"},{"v":0.7591666666666667,"d":"0.76"},{"v":0.6933333333333334,"d":"0.69"},{"v":0.625,"d":"0.63"},{"v":0.5508333333333334,"d":"0.55"}]
[34,30]
[null,31,{"v":34,"d":"latitud = 34 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,32,null,"Enero",{"v":1,"d":"1.00"},1.06,1.12,1.17,1.21,1.25,1.27,1.29,1.31,1.31,1.31,{"v":1.3,"d":"1.30"},1.28,1.25,1.21,1.17,1.12,1.06,{"v":1,"d":"1.00"}]
[null,33,null,"Febrero",{"v":1,"d":"1.00"},1.05,{"v":1.1,"d":"1.10"},1.13,1.16,1.19,{"v":1.2,"d":"1.20"},1.21,1.21,1.21,1.19,1.17,1.14,1.11,1.06,1.01,0.96,{"v":0.9,"d":"0.90"},0.83]
[null,34,null,"Marzo",{"v":1,"d":"1.00"},1.04,1.07,1.09,1.11,1.12,1.12,1.11,{"v":1.1,"d":"1.10"},1.08,1.05,1.02,0.98,0.93,0.88,0.82,0.76,0.69,0.62]
[null,35,null,"Abril",{"v":1,"d":"1.00"},1.02,1.04,1.05,1.05,1.04,1.03,1.01,0.98,0.95,0.91,0.86,0.81,0.75,0.69,0.63,0.53,0.48,0.41]
[null,36,null,"Mayo",{"v":1,"d":"1.00"},1.01,1.01,1.01,{"v":1,"d":"1.00"},0.98,0.96,0.93,0.89,0.85,{"v":0.8,"d":"0.80"},0.75,0.69,0.63,0.56,0.49,0.41,0.34,0.26]
[null,37,null,"Junio",{"v":1,"d":"1.00"},1.01,1.01,{"v":1,"d":"1.00"},0.98,0.96,0.94,{"v":0.9,"d":"0.90"},0.86,0.81,0.76,{"v":0.7,"d":"0.70"},0.64,0.58,0.51,0.43,0.36,0.28,{"v":0.2,"d":"0.20"}]
[null,38,null,"Julio",{"v":1,"d":"1.00"},1.01,1.02,1.01,{"v":1,"d":"1.00"},0.99,0.96,0.93,0.89,0.85,{"v":0.8,"d":"0.80"},0.75,0.69,0.62,0.55,0.48,0.41,0.33,0.25]
[null,39,null,"Agosto",{"v":1,"d":"1.00"},1.02,1.04,1.05,1.05,1.05,1.03,1.01,0.99,0.95,0.91,0.87,0.82,0.76,0.69,0.63,0.56,0.48,{"v":0.4,"d":"0.40"}]
[null,40,null,"Septiembre",{"v":1,"d":"1.00"},1.04,1.08,1.11,1.13,1.14,1.14,1.14,1.13,1.11,1.09,1.05,1.01,0.96,0.91,0.85,0.78,0.71,0.64]
[null,41,null,"Octubre",{"v":1,"d":"1.00"},1.06,1.12,1.17,1.21,1.24,1.27,1.28,1.29,1.29,1.28,1.26,1.23,{"v":1.2,"d":"1.20"},1.15,{"v":1.1,"d":"1.10"},1.04,0.98,0.91]
[null,42,null,"Noviembre",{"v":1,"d":"1.00"},1.08,1.14,1.21,1.26,1.31,1.34,1.37,1.39,{"v":1.4,"d":"1.40"},1.41,{"v":1.4,"d":"1.40"},1.38,1.36,1.32,1.28,1.23,1.17,{"v":1.1,"d":"1.10"}]
[null,43,null,"Diciembre",{"v":1,"d":"1.00"},1.07,1.14,{"v":1.2,"d":"1.20"},1.25,{"v":1.3,"d":"1.30"},1.33,1.36,1.38,{"v":1.4,"d":"1.40"},{"v":1.4,"d":"1.40"},1.39,1.38,1.36,1.32,1.28,1.27,1.18,1.12]
[null,44,null,"Media anual",{"v":1,"d":"1.00"},{"v":1.0391666666666666,"d":"1.04"},{"v":1.0741666666666667,"d":"1.07"},{"v":1.0999999999999999,"d":"1.10"},{"v":1.1175000000000002,"d":"1.12"},{"v":1.1308333333333336,"d":"1.13"},{"v":1.1325,"d":"1.13"},{"v":1.1283333333333332,"d":"1.13"},{"v":1.1183333333333332,"d":"1.12"},{"v":1.100833333333333,"d":"1.10"},{"v":1.0758333333333334,"d":"1.08"},{"v":1.0433333333333334,"d":"1.04"},{"v":1.0041666666666667,"d":"1.00"},{"v":0.9591666666666666,"d":"0.96"},{"v":0.9041666666666668,"d":"0.90"},{"v":0.8474999999999998,"d":"0.85"},{"v":0.7858333333333335,"d":"0.79"},{"v":0.7166666666666667,"d":"0.72"},{"v":0.6450000000000001,"d":"0.65"}]
[35,45]
[null,46,{"v":35,"d":"latitud = 35 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,47,null,"Enero",{"v":1,"d":"1.00"},1.06,1.12,1.17,1.22,1.25,1.28,1.31,1.32,1.33,1.32,1.31,1.29,1.27,1.23,1.19,1.14,1.09,1.02]
[null,48,null,"Febrero",{"v":1,"d":"1.00"},1.05,{"v":1.1,"d":"1.10"},1.14,1.17,{"v":1.2,"d":"1.20"},1.21,1.22,1.23,1.22,1.21,1.19,1.16,1.12,1.08,1.03,0.98,0.92,0.85]
[null,49,null,"Marzo",{"v":1,"d":"1.00"},1.04,1.07,1.09,1.11,1.12,1.13,1.12,1.11,1.09,1.07,1.03,0.99,0.95,{"v":0.9,"d":"0.90"},0.84,0.78,0.71,0.64]
[null,50,null,"Abril",{"v":1,"d":"1.00"},1.02,1.04,1.05,1.05,1.05,1.04,1.02,0.99,0.96,0.92,0.87,0.82,0.77,0.71,0.64,0.57,{"v":0.5,"d":"0.50"},0.42]
[null,51,null,"Mayo",{"v":1,"d":"1.00"},1.01,1.02,1.02,1.01,0.99,0.97,0.94,{"v":0.9,"d":"0.90"},0.86,0.81,0.76,{"v":0.7,"d":"0.70"},0.64,0.57,{"v":0.5,"d":"0.50"},0.43,0.35,0.27]
[null,52,null,"Junio",{"v":1,"d":"1.00"},1.01,1.01,{"v":1,"d":"1.00"},0.99,0.97,0.94,0.91,0.87,0.82,0.77,0.72,0.66,0.59,0.52,0.45,0.37,0.29,0.21]
[null,53,null,"Julio",{"v":1,"d":"1.00"},1.01,1.02,1.02,1.01,0.99,0.97,0.94,{"v":0.9,"d":"0.90"},0.86,0.81,0.76,{"v":0.7,"d":"0.70"},0.64,0.57,{"v":0.5,"d":"0.50"},0.42,0.34,0.26]
[null,54,null,"Agosto",{"v":1,"d":"1.00"},1.03,1.04,1.05,1.06,1.05,1.04,1.02,{"v":1,"d":"1.00"},0.97,0.93,0.88,0.83,0.77,0.71,0.64,0.57,{"v":0.5,"d":"0.50"},0.42]
[null,55,null,"Septiembre",{"v":1,"d":"1.00"},1.04,1.08,1.11,1.13,1.15,1.15,1.15,1.14,1.13,{"v":1.1,"d":"1.10"},1.07,1.03,0.98,0.93,0.87,{"v":0.8,"d":"0.80"},0.73,0.66]
[null,56,null,"Octubre",{"v":1,"d":"1.00"},1.06,1.12,1.17,1.22,1.25,1.28,1.29,{"v":1.3,"d":"1.30"},{"v":1.3,"d":"1.30"},{"v":1.3,"d":"1.30"},1.28,1.25,1.22,1.18,1.13,1.07,{"v":1,"d":"1.00"},0.93]
[null,57,null,"Noviembre",{"v":1,"d":"1.00"},1.08,1.15,1.21,1.27,1.32,1.36,1.39,1.41,1.42,1.43,1.42,1.41,1.38,1.35,1.31,1.26,{"v":1.2,"d":"1.20"},1.13]
[null,58,null,"Diciembre",{"v":1,"d":"1.00"},1.07,1.14,1.21,1.26,1.31,1.35,1.38,{"v":1.4,"d":"1.40"},1.41,1.42,1.41,{"v":1.4,"d":"1.40"},1.38,1.35,1.31,1.26,1.21,1.15]
[null,59,null,"Media anual",{"v":1,"d":"1.00"},1.04,{"v":1.0758333333333332,"d":"1.08"},{"v":1.1033333333333333,"d":"1.10"},{"v":1.125,"d":"1.13"},{"v":1.1375000000000002,"d":"1.14"},{"v":1.1433333333333333,"d":"1.14"},{"v":1.1408333333333331,"d":"1.14"},{"v":1.1308333333333336,"d":"1.13"},{"v":1.114166666666667,"d":"1.11"},{"v":1.0908333333333333,"d":"1.09"},{"v":1.0583333333333333,"d":"1.06"},{"v":1.0200000000000002,"d":"1.02"},{"v":0.9758333333333331,"d":"0.98"},{"v":0.9249999999999999,"d":"0.93"},{"v":0.8675,"d":"0.87"},{"v":0.8041666666666667,"d":"0.80"},{"v":0.7366666666666667,"d":"0.74"},{"v":0.6633333333333332,"d":"0.66"}]
[36,60]
[null,61,{"v":36,"d":"latitud = 36 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,62,null,"Enero",{"v":1,"d":"1.00"},1.07,1.13,1.18,1.22,1.26,1.29,1.32,1.33,1.34,1.34,1.33,1.31,1.29,1.25,1.21,1.16,1.11,1.05]
[null,63,null,"Febrero",{"v":1,"d":"1.00"},1.05,{"v":1.1,"d":"1.10"},1.14,1.18,{"v":1.2,"d":"1.20"},1.22,1.23,1.24,1.23,1.22,{"v":1.2,"d":"1.20"},1.17,1.14,{"v":1.1,"d":"1.10"},1.05,{"v":1,"d":"1.00"},0.94,0.87]
[null,64,null,"Marzo",{"v":1,"d":"1.00"},1.04,1.07,{"v":1.1,"d":"1.10"},1.12,1.13,1.13,1.13,1.12,{"v":1.1,"d":"1.10"},1.08,1.05,1.01,0.96,0.91,0.85,0.79,0.73,0.65]
[null,65,null,"Abril",{"v":1,"d":"1.00"},1.02,1.04,1.05,1.06,1.05,1.04,1.02,{"v":1,"d":"1.00"},0.97,0.93,0.89,0.84,0.78,0.72,0.66,0.59,0.52,0.44]
[null,66,null,"Mayo",{"v":1,"d":"1.00"},1.01,1.02,1.02,1.01,{"v":1,"d":"1.00"},0.98,0.95,0.91,0.87,0.82,0.77,0.71,0.65,0.59,0.52,0.44,0.37,0.29]
[null,67,null,"Junio",{"v":1,"d":"1.00"},1.01,1.01,1.01,0.99,0.98,0.95,0.92,0.88,0.84,0.78,0.73,0.67,{"v":0.6,"d":"0.60"},0.53,0.46,0.39,0.31,0.23]
[null,68,null,"Julio",{"v":1,"d":"1.00"},1.01,1.02,1.02,1.01,{"v":1,"d":"1.00"},0.98,0.95,0.91,0.87,0.82,0.77,0.71,0.65,0.58,0.51,0.44,0.36,0.28]
[null,69,null,"Agosto",{"v":1,"d":"1.00"},1.03,1.05,1.06,1.06,1.06,1.05,1.03,1.01,0.98,0.94,{"v":0.9,"d":"0.90"},0.84,0.79,0.73,0.66,0.59,0.51,0.44]
[null,70,null,"Septiembre",{"v":1,"d":"1.00"},1.05,1.08,1.12,1.14,1.16,1.16,1.16,1.16,1.14,1.12,1.08,1.05,{"v":1,"d":"1.00"},0.95,0.89,0.82,0.75,0.68]
[null,71,null,"Octubre",{"v":1,"d":"1.00"},1.07,1.13,1.18,1.22,1.26,1.29,1.31,1.32,1.32,1.31,{"v":1.3,"d":"1.30"},1.27,1.24,{"v":1.2,"d":"1.20"},1.15,1.09,1.03,0.96]
[null,72,null,"Noviembre",{"v":1,"d":"1.00"},1.08,1.15,1.22,1.28,1.33,1.37,{"v":1.4,"d":"1.40"},1.43,1.44,1.45,1.44,1.43,1.41,1.37,1.33,1.28,1.23,1.16]
[null,73,null,"Diciembre",{"v":1,"d":"1.00"},1.08,1.15,1.21,1.27,1.32,1.36,1.39,1.41,1.43,1.44,1.43,1.42,{"v":1.4,"d":"1.40"},1.37,1.33,1.29,1.23,1.17]
[null,74,null,"Media anual",{"v":1,"d":"1.00"},{"v":1.0433333333333332,"d":"1.04"},{"v":1.0791666666666666,"d":"1.08"},{"v":1.1091666666666666,"d":"1.11"},{"v":1.1300000000000001,"d":"1.13"},{"v":1.1458333333333333,"d":"1.15"},{"v":1.1516666666666666,"d":"1.15"},{"v":1.1508333333333334,"d":"1.15"},{"v":1.1433333333333333,"d":"1.14"},{"v":1.1275000000000002,"d":"1.13"},{"v":1.1041666666666667,"d":"1.10"},{"v":1.0741666666666667,"d":"1.07"},{"v":1.0358333333333334,"d":"1.04"},{"v":0.9925,"d":"0.99"},{"v":0.9416666666666668,"d":"0.94"},{"v":0.8849999999999999,"d":"0.89"},{"v":0.8233333333333333,"d":"0.82"},{"v":0.7575,"d":"0.76"},{"v":0.6849999999999999,"d":"0.69"}]
[37,75]
[null,76,{"v":37,"d":"latitud = 37 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,77,null,"Enero",{"v":1,"d":"1.00"},1.07,1.13,1.18,1.23,1.27,{"v":1.3,"d":"1.30"},1.33,1.35,1.35,1.35,1.35,1.33,1.31,1.27,1.23,1.19,1.13,1.07]
[null,78,null,"Febrero",{"v":1,"d":"1.00"},{"v":10.6,"d":"10.60"},{"v":1.1,"d":"1.10"},1.15,1.18,1.21,1.23,1.24,1.25,1.25,1.24,1.22,1.19,1.16,1.12,1.07,1.02,0.96,0.89]
[null,79,null,"Marzo",{"v":1,"d":"1.00"},{"v":10.4,"d":"10.40"},1.08,{"v":1.1,"d":"1.10"},1.12,1.14,1.14,1.14,1.13,1.11,1.09,1.06,1.02,0.98,0.93,0.87,0.81,0.74,0.67]
[null,80,null,"Abril",{"v":1,"d":"1.00"},{"v":10.3,"d":"10.30"},1.05,1.06,1.06,1.06,1.05,1.03,1.01,0.98,0.94,{"v":0.9,"d":"0.90"},0.85,{"v":0.8,"d":"0.80"},0.74,0.67,{"v":0.6,"d":"0.60"},0.53,0.46]
[null,81,null,"Mayo",{"v":1,"d":"1.00"},1.01,1.02,1.02,1.02,{"v":1,"d":"1.00"},0.98,0.96,0.92,0.88,0.84,0.78,0.73,0.67,{"v":0.6,"d":"0.60"},0.53,0.46,0.38,{"v":0.3,"d":"0.30"}]
[null,82,null,"Junio",{"v":1,"d":"1.00"},1.01,1.01,1.01,{"v":1,"d":"1.00"},0.98,0.96,0.93,0.89,0.85,{"v":0.8,"d":"0.80"},0.74,0.68,0.62,0.55,0.48,{"v":0.4,"d":"0.40"},0.32,0.25]
[null,83,null,"Julio",{"v":1,"d":"1.00"},1.02,1.02,1.02,1.02,{"v":1,"d":"1.00"},0.98,0.96,0.92,0.88,0.84,0.78,0.73,0.66,{"v":0.6,"d":"0.60"},0.53,0.45,0.38,{"v":0.3,"d":"0.30"}]
[null,84,null,"Agosto",{"v":1,"d":"1.00"},1.03,1.05,1.06,1.07,1.07,1.06,1.04,1.02,0.99,0.95,0.91,0.86,{"v":0.8,"d":"0.80"},0.74,0.68,{"v":0.6,"d":"0.60"},0.53,0.45]
[null,85,null,"Septiembre",{"v":1,"d":"1.00"},1.05,1.09,1.12,1.15,1.16,1.17,1.17,1.17,1.15,1.13,{"v":1.1,"d":"1.10"},1.06,1.02,0.97,0.91,0.84,0.77,{"v":0.7,"d":"0.70"}]
[null,86,null,"Octubre",{"v":1,"d":"1.00"},1.07,1.13,1.19,1.23,1.27,{"v":1.3,"d":"1.30"},1.32,1.34,1.34,1.33,1.32,{"v":1.3,"d":"1.30"},1.26,1.22,1.17,1.12,1.05,0.98]
[null,87,null,"Noviembre",{"v":1,"d":"1.00"},1.08,1.16,1.23,1.29,1.34,1.38,1.42,1.44,1.46,1.47,1.47,1.45,1.43,{"v":1.4,"d":"1.40"},{"v":1.6,"d":"1.60"},1.31,1.26,1.19]
[null,88,null,"Diciembre",{"v":1,"d":"1.00"},1.08,1.15,1.22,1.28,1.33,1.37,1.41,1.43,1.45,1.46,1.45,1.44,1.42,{"v":1.4,"d":"1.40"},1.36,1.31,1.26,{"v":1.2,"d":"1.20"}]
[null,89,null,"Media anual",{"v":1,"d":"1.00"},{"v":3.393333333333333,"d":"3.39"},{"v":1.0825,"d":"1.08"},{"v":1.1133333333333333,"d":"1.11"},{"v":1.1375,"d":"1.14"},{"v":1.1525,"d":"1.15"},{"v":1.1600000000000001,"d":"1.16"},{"v":1.1624999999999999,"d":"1.16"},{"v":1.1558333333333333,"d":"1.16"},{"v":1.1408333333333331,"d":"1.14"},1.12,1.09,{"v":1.0533333333333332,"d":"1.05"},{"v":1.0108333333333333,"d":"1.01"},{"v":0.9616666666666668,"d":"0.96"},{"v":0.9249999999999999,"d":"0.93"},{"v":0.8425000000000001,"d":"0.84"},{"v":0.7758333333333334,"d":"0.78"},{"v":0.705,"d":"0.71"}]
[38,90]
[null,91,{"v":38,"d":"latitud = 38 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,92,null,"Enero",{"v":1,"d":"1.00"},1.07,1.13,1.19,1.24,1.28,1.31,1.34,1.36,1.37,1.37,1.36,1.35,1.33,1.29,1.25,1.21,1.15,1.09]
[null,93,null,"Febrero",{"v":1,"d":"1.00"},1.06,1.11,1.15,1.19,1.22,1.24,1.25,1.26,1.26,1.25,1.23,1.21,1.18,1.14,1.09,1.04,0.98,0.91]
[null,94,null,"Marzo",{"v":1,"d":"1.00"},1.04,1.08,1.11,1.13,1.14,1.15,1.15,1.14,1.13,{"v":1.1,"d":"1.10"},1.07,1.04,0.99,0.94,0.89,0.83,0.76,0.69]
[null,95,null,"Abril",{"v":1,"d":"1.00"},1.03,1.05,1.06,1.07,1.07,1.06,1.04,1.02,0.99,0.96,0.91,0.86,0.81,0.75,0.69,0.62,0.55,0.47]
[null,96,null,"Mayo",{"v":1,"d":"1.00"},1.02,1.02,1.03,1.02,1.01,0.99,0.96,0.93,0.89,0.85,{"v":0.8,"d":"0.80"},0.74,0.68,0.61,0.54,0.47,{"v":0.4,"d":"0.40"},0.32]
[null,97,null,"Junio",{"v":1,"d":"1.00"},1.01,1.02,1.01,1.01,0.99,0.97,0.94,{"v":0.9,"d":"0.90"},0.86,0.81,0.75,0.69,0.63,0.56,0.49,0.42,0.34,0.26]
[null,98,null,"Julio",{"v":1,"d":"1.00"},1.02,1.03,1.03,1.02,1.01,0.99,0.97,0.93,0.89,0.85,{"v":0.8,"d":"0.80"},0.74,0.68,0.61,0.54,0.47,0.39,0.31]
[null,99,null,"Agosto",{"v":1,"d":"1.00"},1.03,1.05,1.07,1.07,1.08,1.07,1.05,1.03,{"v":1,"d":"1.00"},0.97,0.92,0.87,0.82,0.76,0.69,0.62,0.55,0.47]
[null,100,null,"Septiembre",{"v":1,"d":"1.00"},1.05,1.09,1.13,1.15,1.17,1.18,1.19,1.18,1.17,1.15,1.12,1.08,1.04,0.98,0.93,0.86,0.79,0.72]
[null,101,null,"Octubre",{"v":1,"d":"1.00"},1.07,1.14,1.19,1.24,1.28,1.31,1.34,1.35,1.36,1.35,1.34,1.32,1.29,1.25,{"v":1.2,"d":"1.20"},1.14,1.08,1.01]
[null,102,null,"Noviembre",{"v":1,"d":"1.00"},1.08,1.16,1.23,{"v":1.3,"d":"1.30"},1.35,{"v":1.4,"d":"1.40"},1.43,1.46,1.48,1.49,1.49,1.48,1.46,1.43,1.39,1.34,1.29,1.22]
[null,103,null,"Diciembre",{"v":1,"d":"1.00"},1.08,1.16,1.22,1.29,1.34,1.38,1.42,1.45,1.47,1.48,1.48,1.47,1.45,1.42,1.39,1.34,1.29,1.23]
[null,104,null,"Media anual",{"v":1,"d":"1.00"},{"v":1.0466666666666666,"d":"1.05"},{"v":1.0866666666666667,"d":"1.09"},{"v":1.1183333333333334,"d":"1.12"},{"v":1.1441666666666668,"d":"1.14"},{"v":1.1616666666666666,"d":"1.16"},{"v":1.1708333333333334,"d":"1.17"},{"v":1.1733333333333331,"d":"1.17"},{"v":1.1674999999999998,"d":"1.17"},{"v":1.1558333333333335,"d":"1.16"},{"v":1.1358333333333335,"d":"1.14"},{"v":1.1058333333333334,"d":"1.11"},{"v":1.0708333333333335,"d":"1.07"},1.03,{"v":0.9783333333333332,"d":"0.98"},{"v":0.9241666666666667,"d":"0.92"},{"v":0.8633333333333333,"d":"0.86"},{"v":0.7975,"d":"0.80"},{"v":0.725,"d":"0.73"}]
[39,105]
[null,106,{"v":39,"d":"latitud = 39 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,107,null,"Enero",1,1.07,1.14,1.19,1.25,1.29,1.33,1.35,1.37,1.38,1.39,1.38,1.37,1.35,1.32,1.28,1.23,1.18,1.12]
[null,108,null,"Febrero",1,1.06,1.11,1.16,1.2,1.23,1.25,1.27,1.27,1.27,1.26,1.25,1.22,1.19,1.15,1.11,1.06,1,0.93]
[null,109,null,"Marzo",1,1.04,1.08,1.11,1.14,1.15,1.16,1.16,1.15,1.14,1.12,1.09,1.05,1.01,0.96,0.91,0.84,0.78,0.71]
[null,110,null,"Abril",1,1.03,1.05,1.07,1.07,1.07,1.07,1.05,1.03,1,0.97,0.93,0.88,0.83,0.77,0.7,0.64,0.56,0.49]
[null,111,null,"Mayo",1,1.02,1.03,1.03,1.03,1.02,1,0.97,0.94,0.9,0.86,0.81,0.75,0.69,0.63,0.56,0.49,0.41,0.33]
[null,112,null,"Junio",1,1.01,1.02,1.02,1.01,1,0.97,0.94,0.91,0.87,0.82,0.77,0.71,0.65,0.58,0.51,0.43,0.35,0.28]
[null,113,null,"Julio",1,1.02,1.03,1.03,1.03,1.02,1,0.98,0.94,0.9,0.86,0.81,0.75,0.69,0.63,0.56,0.48,0.41,0.33]
[null,114,null,"Agosto",1,1.03,1.06,1.07,1.08,1.08,1.08,1.06,1.04,1.01,0.98,0.94,0.89,0.83,0.77,0.71,0.64,0.56,0.49]
[null,115,null,"Septiembre",1,1.05,1.1,1.13,1.16,1.18,1.19,1.2,1.19,1.18,1.16,1.13,1.1,1.05,1,0.95,0.88,0.81,0.74]
[null,116,null,"Octubre",1,1.07,1.14,1.2,1.25,1.29,1.33,1.35,1.37,1.37,1.37,1.36,1.34,1.31,1.27,1.23,1.17,1.11,1.04]
[null,117,null,"Noviembre",1,1.09,1.17,1.24,1.31,1.36,1.41,1.45,1.48,1.5,1.51,1.51,1.51,1.49,1.46,1.42,1.37,1.32,1.25]
[null,118,null,"Diciembre",1,1.08,1.16,1.23,1.29,1.35,1.4,1.43,1.46,1.48,1.5,1.5,1.49,1.47,1.45,1.41,1.37,1.32,1.26]
[null,119,null,"Media anual",{"v":1,"d":"1.00"},{"v":1.0475,"d":"1.05"},{"v":1.0908333333333333,"d":"1.09"},{"v":1.1233333333333333,"d":"1.12"},{"v":1.1516666666666666,"d":"1.15"},{"v":1.1699999999999997,"d":"1.17"},{"v":1.1824999999999999,"d":"1.18"},{"v":1.1841666666666666,"d":"1.18"},{"v":1.1791666666666665,"d":"1.18"},{"v":1.1666666666666667,"d":"1.17"},{"v":1.1500000000000001,"d":"1.15"},{"v":1.1233333333333333,"d":"1.12"},{"v":1.0883333333333332,"d":"1.09"},{"v":1.0466666666666669,"d":"1.05"},{"v":0.9991666666666665,"d":"1.00"},{"v":0.9458333333333334,"d":"0.95"},{"v":0.8833333333333334,"d":"0.88"},{"v":0.8175,"d":"0.82"},{"v":0.7475,"d":"0.75"}]
[40,120]
[null,121,{"v":40,"d":"latitud = 40 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,122,null,"Enero",{"v":1,"d":"1.00"},1.07,1.14,{"v":1.2,"d":"1.20"},1.25,1.13,{"v":1.134,"d":"1.13"},1.37,1.39,{"v":1.4,"d":"1.40"},1.41,{"v":1.4,"d":"1.40"},1.39,1.37,{"v":1.034,"d":"1.03"},{"v":1.3,"d":"1.30"},1.25,{"v":1.2,"d":"1.20"},1.14]
[null,123,null,"Febrero",{"v":1,"d":"1.00"},1.06,1.11,1.16,{"v":1.2,"d":"1.20"},1.23,1.26,1.28,1.29,1.29,1.28,1.27,1.24,1.21,1.17,1.13,1.08,1.02,0.95]
[null,124,null,"Marzo",{"v":1,"d":"1.00"},1.05,1.08,1.12,1.14,1.16,1.17,1.17,1.16,1.15,1.13,{"v":1.1,"d":"1.10"},1.07,1.03,0.98,0.92,0.86,{"v":0.8,"d":"0.80"},0.73]
[null,125,null,"Abril",{"v":1,"d":"1.00"},1.03,1.05,1.07,1.08,1.08,1.07,1.06,1.04,1.01,0.98,0.94,0.89,0.84,0.78,0.72,0.65,0.58,{"v":0.5,"d":"0.50"}]
[null,126,null,"Mayo",{"v":1,"d":"1.00"},1.02,1.03,1.03,1.03,1.02,1.01,0.98,0.95,0.91,0.87,0.82,0.77,0.71,0.64,0.57,{"v":0.5,"d":"0.50"},0.43,0.35]
[null,127,null,"Junio",{"v":1,"d":"1.00"},1.01,1.02,1.02,1.02,{"v":1,"d":"1.00"},0.98,0.95,0.92,0.88,0.83,0.78,0.72,0.66,0.59,0.52,0.45,0.37,0.29]
[null,128,null,"Julio",{"v":1,"d":"1.00"},1.02,1.03,1.04,1.03,1.02,1.01,0.98,0.95,0.92,0.87,0.82,0.77,0.71,0.64,0.57,{"v":0.5,"d":"0.50"},0.42,0.34]
[null,129,null,"Agosto",{"v":1,"d":"1.00"},1.03,1.06,1.08,1.09,1.09,1.09,1.07,1.05,1.03,0.99,0.95,{"v":0.9,"d":"0.90"},0.85,0.79,0.73,0.66,0.58,{"v":0.5,"d":"0.50"}]
[null,130,null,"Septiembre",{"v":1,"d":"1.00"},1.05,{"v":1.1,"d":"1.10"},1.14,1.17,1.19,{"v":1.2,"d":"1.20"},1.21,1.21,{"v":1.2,"d":"1.20"},1.18,1.15,1.12,1.07,1.02,0.97,{"v":0.9,"d":"0.90"},0.84,0.76]
[null,131,null,"Octubre",{"v":1,"d":"1.00"},1.08,1.14,1.21,1.26,{"v":1.3,"d":"1.30"},1.34,1.37,1.39,1.39,1.39,1.38,1.36,1.34,{"v":1.3,"d":"1.30"},1.25,{"v":1.2,"d":"1.20"},1.14,1.07]
[null,132,null,"Noviembre",{"v":1,"d":"1.00"},1.09,1.17,1.25,1.32,1.38,1.43,1.47,{"v":1.5,"d":"1.50"},1.52,1.54,1.54,1.53,1.51,1.49,1.45,1.41,1.35,1.29]
[null,133,null,"Diciembre",{"v":1,"d":"1.00"},1.09,1.16,1.24,{"v":1.3,"d":"1.30"},1.36,1.41,1.45,1.48,{"v":1.5,"d":"1.50"},1.52,1.52,1.51,{"v":1.5,"d":"1.50"},1.47,1.44,{"v":1.4,"d":"1.40"},1.35,1.29]
[null,134,null,"Media anual",{"v":1,"d":"1.00"},1.05,{"v":1.0908333333333333,"d":"1.09"},{"v":1.1300000000000001,"d":"1.13"},{"v":1.1575000000000002,"d":"1.16"},{"v":1.163333333333333,"d":"1.16"},{"v":1.1753333333333333,"d":"1.18"},{"v":1.1966666666666668,"d":"1.20"},{"v":1.1941666666666668,"d":"1.19"},{"v":1.1833333333333333,"d":"1.18"},{"v":1.1658333333333333,"d":"1.17"},{"v":1.1391666666666664,"d":"1.14"},{"v":1.1058333333333332,"d":"1.11"},{"v":1.0666666666666667,"d":"1.07"},{"v":0.992,"d":"0.99"},{"v":0.9641666666666665,"d":"0.96"},{"v":0.9050000000000001,"d":"0.91"},{"v":0.8399999999999999,"d":"0.84"},{"v":0.7675000000000001,"d":"0.77"}]
[41,135]
[null,136,{"v":41,"d":"latitud = 41 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,137,null,"Enero",{"v":1,"d":"1.00"},1.07,{"v":1.114,"d":"1.11"},1.21,1.26,1.31,1.35,1.38,{"v":1.4,"d":"1.40"},1.42,1.42,1.42,1.41,1.39,1.36,1.32,1.28,1.23,1.17]
[null,138,null,"Febrero",{"v":1,"d":"1.00"},1.06,1.12,1.17,1.21,1.24,1.27,{"v":1.2,"d":"1.20"},{"v":1.3,"d":"1.30"},{"v":1.3,"d":"1.30"},{"v":1.3,"d":"1.30"},1.28,1.26,1.23,1.19,1.15,{"v":1.1,"d":"1.10"},1.04,0.98]
[null,139,null,"Marzo",{"v":1,"d":"1.00"},1.05,1.09,1.12,1.15,1.17,1.18,1.18,1.18,1.16,1.14,1.12,1.08,1.04,0.99,0.94,0.88,0.82,0.74]
[null,140,null,"Abril",{"v":1,"d":"1.00"},1.03,1.06,1.07,1.08,1.09,1.08,1.07,1.05,1.03,0.99,0.95,0.91,0.85,{"v":0.8,"d":"0.80"},0.73,0.67,{"v":0.6,"d":"0.60"},0.52]
[null,141,null,"Mayo",{"v":1,"d":"1.00"},1.02,1.03,1.04,1.04,1.03,1.01,0.99,0.96,0.93,0.88,0.83,0.78,0.72,0.66,0.59,0.52,0.44,0.36]
[null,142,null,"Junio",{"v":1,"d":"1.00"},1.02,1.02,1.03,1.02,1.01,0.99,0.96,0.93,0.89,0.84,0.79,0.73,0.67,0.61,0.54,0.46,0.39,0.31]
[null,143,null,"Julio",{"v":1,"d":"1.00"},1.02,1.03,1.04,1.04,1.03,1.02,0.99,0.96,0.93,0.88,0.84,0.78,0.72,0.66,0.59,0.52,0.44,0.36]
[null,144,null,"Agosto",{"v":1,"d":"1.00"},1.03,1.06,1.08,1.09,{"v":1.1,"d":"1.10"},1.09,1.08,1.06,1.04,1.01,0.97,0.92,0.87,0.81,0.74,0.67,{"v":0.6,"d":"0.60"},0.52]
[null,145,null,"Septiembre",{"v":1,"d":"1.00"},1.05,{"v":1.1,"d":"1.10"},1.14,1.17,{"v":1.2,"d":"1.20"},1.21,1.22,1.22,1.21,1.19,1.17,1.14,1.09,1.04,0.99,0.93,0.86,0.78]
[null,146,null,"Octubre",{"v":1,"d":"1.00"},1.08,1.15,1.21,1.27,1.32,1.35,1.38,{"v":1.4,"d":"1.40"},1.41,1.41,1.41,1.39,1.36,1.32,1.28,1.23,1.16,1.09]
[null,147,null,"Noviembre",{"v":1,"d":"1.00"},1.09,1.18,1.26,1.33,1.39,1.44,1.49,1.52,1.55,1.56,1.57,1.56,1.54,1.52,1.48,1.44,1.38,1.32]
[null,148,null,"Diciembre",{"v":1,"d":"1.00"},1.09,1.17,1.24,1.31,1.37,1.42,1.47,{"v":1.5,"d":"1.50"},1.52,1.54,1.54,1.54,1.53,{"v":1.5,"d":"1.50"},1.47,1.43,1.38,1.32]
[null,149,null,"Media anual",{"v":1,"d":"1.00"},{"v":1.0508333333333333,"d":"1.05"},{"v":1.0936666666666668,"d":"1.09"},{"v":1.134166666666667,"d":"1.13"},{"v":1.1641666666666668,"d":"1.16"},{"v":1.1883333333333335,"d":"1.19"},{"v":1.2008333333333332,"d":"1.20"},{"v":1.2008333333333336,"d":"1.20"},{"v":1.2066666666666668,"d":"1.21"},{"v":1.1991666666666667,"d":"1.20"},1.18,{"v":1.1575,"d":"1.16"},{"v":1.125,"d":"1.13"},{"v":1.0841666666666667,"d":"1.08"},{"v":1.0383333333333333,"d":"1.04"},{"v":0.985,"d":"0.99"},{"v":0.9274999999999999,"d":"0.93"},{"v":0.8616666666666667,"d":"0.86"},{"v":0.7891666666666666,"d":"0.79"}]
[42,150]
[null,151,{"v":42,"d":"latitud = 42 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,152,null,"Enero",{"v":1,"d":"1.00"},1.08,1.15,1.21,1.27,1.32,1.36,1.39,1.42,1.43,1.44,1.44,1.43,1.41,1.38,1.35,{"v":1.3,"d":"1.30"},1.25,1.19]
[null,153,null,"Febrero",{"v":1,"d":"1.00"},1.06,1.12,1.17,1.21,1.25,1.28,{"v":1.3,"d":"1.30"},1.31,1.32,1.31,{"v":1.3,"d":"1.30"},1.28,1.25,1.21,1.17,1.12,1.06,{"v":1,"d":"1.00"}]
[null,154,null,"Marzo",{"v":1,"d":"1.00"},1.05,1.09,1.13,1.15,1.17,1.19,1.19,1.19,1.18,1.16,1.13,{"v":1.1,"d":"1.10"},1.06,{"v":1.1,"d":"1.10"},0.96,{"v":0.9,"d":"0.90"},0.83,0.76]
[null,155,null,"Abril",{"v":1,"d":"1.00"},1.03,1.06,1.08,1.09,1.09,1.09,1.08,1.06,1.04,{"v":1,"d":"1.00"},0.97,0.92,0.87,0.81,0.75,0.68,0.61,0.54]
[null,156,null,"Mayo",{"v":1,"d":"1.00"},1.02,1.04,1.04,1.04,1.04,1.02,{"v":1,"d":"1.00"},0.97,0.94,0.89,0.85,0.79,0.74,0.67,0.6,0.53,0.46,0.38]
[null,157,null,"Junio",{"v":1,"d":"1.00"},1.02,1.03,1.03,1.03,1.01,{"v":1,"d":"1.00"},0.97,0.94,{"v":0.9,"d":"0.90"},0.86,{"v":0.8,"d":"0.80"},0.75,0.69,0.62,0.55,0.48,{"v":0.4,"d":"0.40"},0.32]
[null,158,null,"Julio",{"v":1,"d":"1.00"},1.02,1.04,1.04,1.05,1.04,1.02,{"v":1,"d":"1.00"},0.97,0.94,{"v":0.9,"d":"0.90"},0.85,{"v":0.8,"d":"0.80"},0.74,0.67,{"v":0.6,"d":"0.60"},0.53,0.46,0.38]
[null,159,null,"Agosto",{"v":1,"d":"1.00"},1.04,1.06,1.09,{"v":1.1,"d":"1.10"},{"v":1.1,"d":"1.10"},{"v":1.1,"d":"1.10"},1.09,1.08,1.05,1.02,0.98,0.93,0.88,0.82,0.76,0.69,0.62,0.54]
[null,160,null,"Septiembre",{"v":1,"d":"1.00"},1.06,1.11,1.15,1.18,1.21,1.23,1.23,1.24,1.23,1.21,1.19,1.15,1.11,1.07,1.01,0.95,0.88,0.81]
[null,161,null,"Octubre",{"v":1,"d":"1.00"},1.08,1.15,1.22,1.28,1.33,1.37,{"v":1.4,"d":"1.40"},1.42,1.43,1.44,1.43,1.41,1.39,1.35,1.31,1.25,1.19,1.12]
[null,162,null,"Noviembre",{"v":1,"d":"1.00"},1.09,1.18,1.26,1.34,{"v":1.4,"d":"1.40"},1.46,1.51,1.54,1.57,1.59,1.59,1.59,1.57,1.55,1.52,1.47,1.42,1.36]
[null,163,null,"Diciembre",{"v":1,"d":"1.00"},1.09,1.17,1.25,1.32,1.38,1.44,1.48,1.52,1.54,1.56,1.57,1.57,1.55,1.53,{"v":1.5,"d":"1.50"},1.46,1.41,1.35]
[null,164,null,"Media anual",{"v":1,"d":"1.00"},{"v":1.0533333333333335,"d":"1.05"},{"v":1.0999999999999999,"d":"1.10"},{"v":1.1391666666666669,"d":"1.14"},{"v":1.1716666666666666,"d":"1.17"},{"v":1.195,"d":"1.20"},{"v":1.2133333333333334,"d":"1.21"},1.22,{"v":1.2216666666666667,"d":"1.22"},{"v":1.2141666666666666,"d":"1.21"},{"v":1.1983333333333333,"d":"1.20"},{"v":1.1749999999999998,"d":"1.18"},{"v":1.1433333333333333,"d":"1.14"},{"v":1.1050000000000002,"d":"1.11"},{"v":1.065,"d":"1.07"},{"v":1.0066666666666666,"d":"1.01"},{"v":0.9466666666666667,"d":"0.95"},{"v":0.8825,"d":"0.88"},{"v":0.8125,"d":"0.81"}]
[43,165]
[null,166,{"v":43,"d":"latitud = 43 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,167,null,"Enero",{"v":1,"d":"1.00"},1.08,1.15,1.22,1.28,1.33,1.37,1.41,1.43,1.45,1.46,1.46,1.45,1.43,1.41,{"v":1.7,"d":"1.70"},1.33,1.28,1.22]
[null,168,null,"Febrero",{"v":1,"d":"1.00"},1.07,1.12,1.18,1.22,1.26,1.29,1.31,1.33,1.33,1.33,1.32,{"v":1.3,"d":"1.30"},1.27,1.23,1.19,1.14,1.08,1.02]
[null,169,null,"Marzo",{"v":1,"d":"1.00"},1.05,1.09,1.13,1.16,1.18,{"v":1.2,"d":"1.20"},{"v":1.2,"d":"1.20"},{"v":1.2,"d":"1.20"},1.19,1.17,1.15,1.12,1.08,1.03,0.89,0.92,0.85,0.78]
[null,170,null,"Abril",{"v":1,"d":"1.00"},1.03,1.06,1.08,1.09,{"v":1.1,"d":"1.10"},{"v":1.1,"d":"1.10"},1.09,1.07,1.05,1.02,0.98,0.94,0.89,0.83,0.77,{"v":0.7,"d":"0.70"},0.63,0.56]
[null,171,null,"Mayo",{"v":1,"d":"1.00"},1.02,1.04,1.05,1.05,1.04,1.03,1.01,0.98,0.95,0.91,0.86,0.81,0.75,0.69,0.62,0.55,0.47,{"v":0.4,"d":"0.40"}]
[null,172,null,"Junio",{"v":1,"d":"1.00"},1.02,1.03,1.03,1.03,1.02,{"v":1,"d":"1.00"},0.98,0.95,0.91,0.87,0.82,0.76,{"v":0.7,"d":"0.70"},0.64,0.57,0.49,0.42,0.34]
[null,173,null,"Julio",{"v":1,"d":"1.00"},1.02,1.04,1.05,1.05,1.04,1.03,1.01,0.98,0.95,0.91,0.86,0.81,0.75,0.69,0.62,0.55,0.47,0.39]
[null,174,null,"Agosto",{"v":1,"d":"1.00"},1.04,1.07,1.09,{"v":1.1,"d":"1.10"},1.11,1.11,{"v":1.1,"d":"1.10"},1.09,1.06,1.03,{"v":1,"d":"1.00"},0.95,{"v":0.9,"d":"0.90"},0.84,0.78,0.71,0.64,0.56]
[null,175,null,"Septiembre",{"v":1,"d":"1.00"},1.06,1.11,1.15,1.19,1.22,1.24,1.25,1.25,1.24,1.23,1.21,1.17,{"v":1.3,"d":"1.30"},1.09,1.03,0.97,{"v":0.9,"d":"0.90"},0.83]
[null,176,null,"Octubre",{"v":1,"d":"1.00"},1.08,1.16,1.23,1.29,1.34,1.35,1.42,1.44,1.45,1.46,1.45,1.44,1.41,1.38,1.34,1.28,1.22,1.16]
[null,177,null,"Noviembre",{"v":1,"d":"1.00"},{"v":1.1,"d":"1.10"},1.19,1.27,1.35,1.42,1.48,1.52,1.56,1.59,1.61,1.62,1.62,1.61,1.58,1.55,1.51,1.45,1.39]
[null,178,null,"Diciembre",{"v":1,"d":"1.00"},1.09,1.18,1.26,1.33,{"v":1.4,"d":"1.40"},1.45,{"v":1.5,"d":"1.50"},1.54,1.57,1.58,1.59,1.59,1.58,1.56,1.53,1.49,1.44,1.38]
[null,179,null,"Media anual",{"v":1,"d":"1.00"},{"v":1.055,"d":"1.06"},{"v":1.1033333333333333,"d":"1.10"},{"v":1.145,"d":"1.15"},{"v":1.1783333333333335,"d":"1.18"},{"v":1.205,"d":"1.21"},{"v":1.2208333333333334,"d":"1.22"},{"v":1.2333333333333332,"d":"1.23"},{"v":1.235,"d":"1.24"},{"v":1.2283333333333333,"d":"1.23"},{"v":1.215,"d":"1.22"},{"v":1.1933333333333334,"d":"1.19"},{"v":1.1633333333333333,"d":"1.16"},{"v":1.1391666666666667,"d":"1.14"},{"v":1.0808333333333333,"d":"1.08"},{"v":1.0491666666666666,"d":"1.05"},{"v":0.9699999999999999,"d":"0.97"},{"v":0.9041666666666667,"d":"0.90"},{"v":0.8358333333333334,"d":"0.84"}]
[44,180]
[null,181,{"v":44,"d":"latitud = 44 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,182,null,"Enero",1,1.08,1.16,1.22,1.28,1.34,1.38,1.42,1.45,1.47,1.48,1.48,1.47,1.46,1.43,1.4,1.36,1.31,1.25]
[null,183,null,"Febrero",1,1.07,1.13,1.18,1.23,1.27,1.3,1.32,1.34,1.35,1.34,1.33,1.32,1.29,1.26,1.21,1.16,1.11,1.04]
[null,184,null,"Marzo",1,1.05,1.1,1.13,1.17,1.19,1.2,1.21,1.21,1.2,1.19,1.16,1.13,1.09,1.05,1,0.94,0.87,0.8]
[null,185,null,"Abril",1,1.04,1.06,1.09,1.1,1.11,1.11,1.1,1.08,1.06,1.03,0.99,0.95,0.9,0.85,0.78,0.72,0.65,0.57]
[null,186,null,"Mayo",1,1.02,1.04,1.05,1.05,1.05,1.04,1.02,0.99,0.96,0.92,0.87,0.82,0.76,0.7,0.64,0.56,0.49,0.41]
[null,187,null,"Junio",1,1.02,1.03,1.04,1.04,1.03,1.01,0.99,0.96,0.92,0.88,0.83,0.78,0.72,0.65,0.58,0.51,0.43,0.35]
[null,188,null,"Julio",1,1.02,1.04,1.05,1.06,1.05,1.04,1.02,1,0.96,0.92,0.88,0.82,0.77,0.7,0.64,0.56,0.49,0.41]
[null,189,null,"Agosto",1,1.04,1.07,1.09,1.11,1.12,1.12,1.11,1.1,1.08,1.05,1.01,0.97,0.92,0.86,0.8,0.73,0.66,0.58]
[null,190,null,"Septiembre",1,1.06,1.11,1.16,1.2,1.23,1.25,1.26,1.26,1.26,1.25,1.22,1.19,1.16,1.11,1.06,0.99,0.93,0.85]
[null,191,null,"Octubre",1,1.09,1.16,1.23,1.3,1.35,1.4,1.43,1.46,1.48,1.48,1.48,1.47,1.44,1.41,1.37,1.32,1.26,1.19]
[null,192,null,"Noviembre",1,1.1,1.19,1.28,1.36,1.43,1.49,1.54,1.59,1.62,1.64,1.65,1.65,1.64,1.62,1.59,1.54,1.49,1.43]
[null,193,null,"Diciembre",1,1.1,1.18,1.27,1.34,1.41,1.47,1.52,1.56,1.59,1.61,1.62,1.62,1.61,1.59,1.56,1.52,1.48,1.42]
[null,194,null,"Media anual",{"v":1,"d":"1.00"},{"v":1.0574999999999999,"d":"1.06"},{"v":1.1058333333333332,"d":"1.11"},{"v":1.1491666666666667,"d":"1.15"},{"v":1.1866666666666665,"d":"1.19"},{"v":1.215,"d":"1.22"},{"v":1.2341666666666666,"d":"1.23"},{"v":1.2449999999999999,"d":"1.25"},{"v":1.2500000000000002,"d":"1.25"},{"v":1.2458333333333333,"d":"1.25"},{"v":1.2325000000000002,"d":"1.23"},{"v":1.2100000000000002,"d":"1.21"},{"v":1.1825,"d":"1.18"},{"v":1.1466666666666667,"d":"1.15"},{"v":1.1025,"d":"1.10"},{"v":1.0525,"d":"1.05"},{"v":0.9925,"d":"0.99"},{"v":0.9308333333333333,"d":"0.93"},{"v":0.8583333333333333,"d":"0.86"}]
[45,195]
[null,196,{"v":45,"d":"latitud = 45 º"},"Inclinación",0,5,10,15,20,25,30,35,40,45,50,55,60,65,70,75,80,85,90]
[null,197,null,"Enero",1,1.08,1.16,1.23,1.29,1.35,1.4,1.43,1.46,1.49,1.5,1.5,1.5,1.48,1.46,1.43,1.38,1.33,1.28]
[null,198,null,"Febrero",1,1.07,1.13,1.19,1.24,1.28,1.31,1.34,1.35,1.36,1.36,1.35,1.34,1.31,1.28,1.24,1.19,1.13,1.07]
[null,199,null,"Marzo",1,1.05,1.1,1.14,1.17,1.2,1.21,1.22,1.22,1.22,1.2,1.18,1.15,1.11,1.07,1.02,0.96,0.89,0.82]
[null,200,null,"Abril",1,1.04,1.07,1.09,1.11,1.11,1.12,1.11,1.09,1.07,1.04,1.01,0.97,0.92,0.86,0.8,0.74,0.66,0.59]
[null,201,null,"Mayo",1,1.03,1.04,1.05,1.06,1.06,1.04,1.03,1,0.97,0.93,0.89,0.84,0.78,0.72,0.65,0.58,0.51,0.43]
[null,202,null,"Junio",1,1.02,1.04,1.04,1.04,1.03,1.02,1,0.97,0.93,0.89,0.84,0.79,0.73,0.67,0.6,0.53,0.45,0.37]
[null,203,null,"Julio",1,1.03,1.05,1.06,1.06,1.06,1.05,1.03,1.01,0.97,0.94,0.89,0.84,0.78,0.72,0.65,0.58,0.51,0.43]
[null,204,null,"Agosto",1,1.04,1.07,1.1,1.12,1.13,1.13,1.12,1.11,1.09,1.06,1.03,0.98,0.93,0.88,0.82,0.75,0.67,0.6]
[null,205,null,"Septiembre",1,1.06,1.12,1.17,1.21,1.24,1.26,1.27,1.28,1.28,1.26,1.24,1.21,1.18,1.13,1.08,1.02,0.95,0.88]
[null,206,null,"Octubre",1,1.09,1.17,1.24,1.31,1.36,1.41,1.45,1.48,1.5,1.51,1.5,1.49,1.47,1.44,1.4,1.35,1.29,1.22]
[null,207,null,"Noviembre",1,1.1,1.2,1.29,1.37,1.45,1.51,1.56,1.61,1.64,1.67,1.68,1.68,1.67,1.65,1.62,1.58,1.53,1.47]
[null,208,null,"Diciembre",1,1.1,1.19,1.27,1.35,1.42,1.48,1.53,1.58,1.61,1.63,1.65,1.65,1.64,1.62,1.6,1.56,1.51,1.45]
[null,209,null,"Media anual",{"v":1,"d":"1.00"},{"v":1.0591666666666668,"d":"1.06"},{"v":1.1116666666666666,"d":"1.11"},{"v":1.155833333333333,"d":"1.16"},{"v":1.1941666666666666,"d":"1.19"},{"v":1.2241666666666664,"d":"1.22"},{"v":1.245,"d":"1.25"},{"v":1.2575,"d":"1.26"},{"v":1.2633333333333332,"d":"1.26"},{"v":1.2608333333333333,"d":"1.26"},{"v":1.2491666666666665,"d":"1.25"},1.23,{"v":1.2033333333333334,"d":"1.20"},{"v":1.1666666666666667,"d":"1.17"},{"v":1.125,"d":"1.13"},{"v":1.0758333333333334,"d":"1.08"},{"v":1.0183333333333333,"d":"1.02"},{"v":0.9525,"d":"0.95"},{"v":0.8841666666666664,"d":"0.88"}]
[]
["Fila de Enero según Latitud"]
["latitud","fila"]
[28,2]
[29,17]
[34,32]
[35,47]
[36,62]
[37,77]
[38,92]
[39,107]
[40,122]
[41,137]
[42,152]
[43,167]
[44,182]
[45,197]